Furnish and install as shown on plans in accordance with all codes and authorities having jurisdiction ___ water heater(s) Model B+II WaterWizard B+__/__/ EC, as manufactured by AERCO INTERNATIONAL, INC.

Each heater shall be rated to heat ____ GPM of water from ___ °F to ___ °F when supplied with ___lbs/hr of saturated steam at ___ PSIG to the electronic control valve.

Design & Construction:

Each heater shall be of the vertical, cross-flow, 2-pass, Semi-Instantaneous design, having service water in the shell and steam in the coils.  The ratio of hot water volume to steam volume shall be a minimum of 7:1.  Steam shall travel a minimum distance of 45 feet through the heat exchanger, from point of entrance to point of exit.  To ensure condensate sub-cooling an additional sub-cooling coil shall be incorporated into the last pass of the heat exchanger design.  Condensate temperature shall not exceed ___ °F when incoming domestic water temperature is 110 °F or lower.   An orifice in lieu of a condensate trap shall be required for incoming water temperatures up to 110 °F.

The heat exchanger shall be constructed of multiple, individually replaceable, helically wound coils, capable of withstanding up to 30" WC internal vacuum and having no baffles that could interfere with the natural expansion and contraction of the copper.  Each heater shall automatically self-de-scale for any hard water supply (hard water having 7 - 10-1/2 grains hardness per gallon, as defined by the Water Quality Association).  The heat exchanger design shall be suitable for cleaning by the method of thermal shock.  The coil and riser assembly shall be designed and manufactured in accordance with ASME Section VIII, Div. 1 for not less than 250 PSIG @ 400°F working pressure and temperature.

The water vessel shall be designed to allow no greater than 1 FPS average water velocity when traveling through the shell at design flow conditions to ensure no heat exchanger erosion.  Total domestic water pressure drop through the heater shall not exceed 4 PSI at design flow.  The water pressure vessel shall be designed and manufactured in accordance with ASME section VIII, Div. 1 for not less than 235 PSIG @ 400°F working pressure and temperature. All pressure vessel and heat exchanger surfaces in contact with the domestic water shall be copper or copper alloy.  Materials of construction shall be:   3/16" c.s. shell lined with 0.024" sheet copper, minimum of 0.049" wall copper coils, sch. 80 red brass steam riser and stainless steel top and bottom heads.

Electronic Control System:

The heater shall maintain +/- 2°F Max temperature fluctuation from temperature setpoint at 0% to 100 % load at a constant load and +/- 4°F under normal diversified domestic load conditions.  The system shall consist of an electronic control valve, control panel enclosure housing a PID temperature controller with digital indication of shell outlet water temperature, digital over-temperature limit switch, flow meter for feed-forward sensing,  and feedback sensor.   The limit switch shall close the control valve and open a solenoid valve to function as a secondary water relief valve in an over-temperature condition.

The system shall have the following additional characteristics:

- Controller temperature setpoint range between 50°F to 205°F maximum

- Configured for 120V/1 Phase/60 Hz and 220V/1 Phase/ 50 Hz.

- Easy start-up. Dial in setpoint & walk away.

- The electronic steam control valve shall be manufactured by water heater manufacturer and be of the balanced, pilot-operated type, having a soft seat for ANSI Class VI bubble tight shut-off and equal percentage flow characteristics.  Valves shall be applied directly for specified steam pressure without the need for extraneous PRV's.  The valve shall have the following performance characteristics:

- 50 to 1 Turndown.

- Electronic Actuator with Fail Closed Design-particularly on loss of power

- Time to Full Open Position: 7 seconds on 1 to 2 Inch; 9 seconds on 2 ½ to 4 inch

- Time to Full Closed Position: 7 seconds on 1 to 2 Inch; 9 seconds on 2 ½ to 4 inch, including failsafe mode.

- The PID temperature controller shall incorporate a feed-forward function and be password protected.   The controller either ___shall or ___shall not be capable of remote communications via an optional add-in board that incorporates either: ___ RS-232 port or ___RS-485 port & utilizes the MODBUS protocol for interoperability with Building Automation Systems (BAS).

- Controls interface with BACnet, Lonworks, and N2 shall utilize an  ___ optional AERCO Communications Gateway to act as a MODBUS interface/translator between the BAS and the MODBUS port of the temperature controller.  The AERCO Communications Gateway shall be comprised of a microprocessor based control utilizing the MODBUS protocol to communicate with the temperature controller.  Non-volatile backup of all point mappings and programs shall be internally provided as standard.  Connection between Gateway and individual water heaters shall be “daisy chain” with shielded, twisted pair, low voltage wiring for ease of installation.

- The following information shall be accessible locally at the controller or remotely via the communications port:

- Setpoint – can be changed remotely

- Outlet Temperature

- Over Temperature Alarm

- Control Output Signal to valve

- Water Flow through the heater

Each heater shall be supplied by the manufacturer ready to accept existing steam, condensate and water lines, and furnished with the following packaged accessories:

a. Minimum 1½" thick resilient insulation having "K" value of 0.25 BTU-in/hr-ft2-°F, meeting or exceeding ANSI/ASHRAE/IES standard 90.1-1989.

b. Bronze T & P relief valve, conforming to ANZI Z21.22, set at 150 PSIG/210°F.

c. Inlet steam-side compound vacuum/pressure gauge, condensate outlet union orifice and swing check valve, and 2" bronze ball type shell drain valve.

Warranty:

The heater shall carry the following manufacturer's warranty from date of shipment for domestic water service*:

- Heat Exchanger - The heat exchanger, comprised of the coils and risers, shall carry a non-prorated 10 year guarantee against failure due to thermal shock, mechanical failure, manufacturing or material defect or erosion.

- Pressure vessel - The pressure vessel consisting of shell, liner and heads shall carry a non-prorated 20 year guarantee against leakage due to internal corrosion.

- All other components – Shall carry an 18 month guarantee against failure due to manufacturing or material defect.

*Note to specifying engineer:  The above warranty regards domestic water service. For other services, such as wash down, laundry, etc., and for other details, please contact your local AERCO representative.