## 4 C-Mores-1 ACS
BACnet/IP, BACnet MS/TP, Metasys N2, and LonWorks Points List
4 C-Mores and 1 BMS
Equipment | Point Name | Name | Read Only | BACnet Type:ID | N2 Type | N2 ID | Lon SNVT NAME | Lon SNVT | Lon Direction | ModBus/Unit Addr.
Blr Addr 1
| 01-Fire Rate Out | boilerstate_1 | ü | AV:26 | data float | 1 | nvoBlrState1 | inc count (9) | Output (non-polled) | 30009/1
| 02-Active Setpoint | effectsetpt_1 | ü | AV:27 | data float | 2 | nvoEffSetpt1 | inc count (9) | Output (non-polled) | 30017/1
| 03-Net Remote Setpt | setpt_1 |  | AV:24 | data float | 3 | nviSetpt1 | inc count (9) | Input (non-polling) | 40001/1
| 05-Fire Rate In | boilerload_1 | ü | AV:28 | data float | 5 | nvoBlrLoad1 | inc count (9) | Output (non-polled) | 30018/1
| 06-Outlet Temp | localsuptemp_1 | ü | AV:29 | data float | 6 | nvoLocSupTmp1 | inc count (9) | Output (non-polled) | 30003/1
| 07-Display Code | dispcode_1 | ü | AV:22 | data float | 7 | nvoDispCode1 | inc count (9) | Output (non-polled) | 30001/1
| 08-Unit Status | unitstat_1 | ü | AV:23 | data float | 8 | nvoUnitStat1 | inc count (9) | Output (non-polled) | 30002/1
| 09-Run Cycles | runcycles_1 | ü | AV:42 | data float | 9 | nvoRunCycles1 | 51 | Output (non-polled) | 30012-30013/1
| 10-Run Hours | runhours_1 | ü | AV:43 | data float | 10 | nvoRunHours1 | 51 | Output (non-polled) | 30014-30015/1
Blr Addr 2
| 01-Fire Rate Out | boilerstate_2 | ü | AV:30 | data float | 11 | nvoBlrState2 | inc count (9) | Output (non-polled) | 30009/2
| 02-Active Setpoint | effectsetpt_2 | ü | AV:46 | data float | 12 | nvoEffSetpt2 | inc count (9) | Output (non-polled) | 30017/2
| 03-Net Remote Setpt | setpt_2 |  | AV:47 | data float | 13 | nviSetpt2 | inc count (9) | Input (non-polling) | 40001/2
| 05-Fire Rate In | boilerload_2 | ü | AV:50 | data float | 15 | nvoBlrLoad2 | inc count (9) | Output (non-polled) | 30018/2
| 06-Outlet Temp | localsuptemp_2 | ü | AV:51 | data float | 16 | nvoLocSupTmp2 | inc count (9) | Output (non-polled) | 30003/2
| 07-Display Code | dispcode_2 | ü | AV:52 | data float | 17 | nvoDispCode2 | inc count (9) | Output (non-polled) | 30001/2
| 08-Unit Status | unitstat_2 | ü | AV:53 | data float | 18 | nvoUnitStat2 | inc count (9) | Output (non-polled) | 30002/2
| 09-Run Cycles | runcycles_2 | ü | AV:44 | data float | 19 | nvoRunCycles2 | 51 | Output (non-polled) | 30012-30013/2
| 10-Run Hours | runhours_2 | ü | AV:45 | data float | 20 | nvoRunHours2 | 51 | Output (non-polled) | 30014-30015/2
Blr Addr 3
| 01-Fire Rate Out | boilerstate_3 | ü | AV:54 | data float | 21 | nvoBlrState3 | inc count (9) | Output (non-polled) | 30009/3
| 02-Active Setpoint | effectsetpt_3 | ü | AV:55 | data float | 22 | nvoEffSetpt3 | inc count (9) | Output (non-polled) | 30017/3
| 03-Net Remote Setpt | setpt_3 |  | AV:56 | data float | 23 | nviSetpt3 | inc count (9) | Input (non-polling) | 40001/3
| 05-Fire Rate In | boilerload_3 | ü | AV:60 | data float | 25 | nvoBlrLoad3 | inc count (9) | Output (non-polled) | 30018/3
| 06-Outlet Temp | localsuptemp_3 | ü | AV:61 | data float | 26 | nvoLocSupTmp3 | inc count (9) | Output (non-polled) | 30003/3
| 07-Display Code | dispcode_3 | ü | AV:62 | data float | 27 | nvoDispCode3 | inc count (9) | Output (non-polled) | 30001/3
| 08-Unit Status | unitstat_3 | ü | AV:63 | data float | 28 | nvoUnitStat3 | inc count (9) | Output (non-polled) | 30002/3
| 09-Run Cycles | runcycles_3 | ü | AV:58 | data float | 29 | nvoRunCycles3 | 51 | Output (non-polled) | 30012-30013/3
| 10-Run Hours | runhours_3 | ü | AV:59 | data float | 30 | nvoRunHours3 | 51 | Output (non-polled) | 30014-30015/3
Blr Addr 4
| 01-Fire Rate Out | boilerstate_4 | ü | AV:70 | data float | 31 | nvoBlrState4 | inc count (9) | Output (non-polled) | 30009/4
| 02-Active Setpoint | effectsetpt_4 | ü | AV:71 | data float | 32 | nvoEffSetpt4 | inc count (9) | Output (non-polled) | 30017/4
| 03-Net Remote Setpt | setpt_4 |  | AV:72 | data float | 33 | nviSetpt4 | inc count (9) | Input (non-polling) | 40001/4
| 05-Fire Rate In | boilerload_4 | ü | AV:73 | data float | 35 | nvoBlrLoad4 | inc count (9) | Output (non-polled) | 30018/4
| 06-Outlet Temp | localsuptemp_4 | ü | AV:65 | data float | 36 | nvoLocSupTmp4 | inc count (9) | Output (non-polled) | 30003/4
| 07-Display Code | dispcode_4 | ü | AV:66 | data float | 37 | nvoDispCode4 | inc count (9) | Output (non-polled) | 30001/4
| 08-Unit Status | unitstat_4 | ü | AV:67 | data float | 38 | nvoUnitStat4 | inc count (9) | Output (non-polled) | 30002/4
| 09-Run Cycles | runcycles_4 | ü | AV:68 | data float | 39 | nvoRunCycles4 | 51 | Output (non-polled) | 30012-30013/4
| 10-Run Hours | runhours_4 | ü | AV:69 | data float | 40 | nvoRunHours4 | 51 | Output (non-polled) | 30014-30015/4
BMS Addr 128
| 01-Fire Rate Out | boilerstate_5 | ü | AV:31 | data float | 41 | nvoBlrState | inc count (9) | Output (non-polled) |  | 30005/128
| 02-Header Set Temp | effectsetpt_5 | ü | AV:32 | data float | 42 | nvoEffSetpt | inc count (9) | Output (non-polled) |  | 30006/128
| 03-Net Header Set Temp | setpt_5 |  | AV:33 | data float | 43 | nviSetpt | inc count (9) | Input (non-polling) |  | 40005/128
| 04-Header Temp | localsuptemp_5 | ü | AV:34 | data float | 44 | nvoLocSupTmp | inc count (9) | Output (non-polled) |  | 30002/128
| 05-Outside Air Temp | localoatemp_5 | ü | AV:35 | data float | 45 | nvoLocOATmp | inc count (9) | Output (non-polled) |  | 30003/128
| 06-Display Code | dispcode_5 | ü | AV:36 | data float | 46 | nvoDispCode | inc count (9) | Output (non-polled) |  | 30011/128
| 07-Num Boilers Fired | blrfired_5 | ü | AV:37 | data float | 47 | nvoBlrsFired | inc count (9) | Output (non-polled) |  | 30008/128
| 08-Num Boilers Online | blronline_5 | ü | AV:38 | data float | 48 | nvoBlrsOnline | inc count (9) | Output (non-polled) |  | 30009/128
| 09-Last Blr Fired | blrlast_5 | ü | AV:39 | data float | 49 | nvoLastBlrFired | inc count (9) | Output (non-polled) |  | 30017/128
| 10-Boiler 1 Status | blr1stat_5 | ü | AV:40 | data float | 50 | nvoBlr1Stat | inc count (9) | Output (non-polled) |  | 30018/128
| 11-Boiler 2 Status | blr2stat_5 | ü | AV:41 | data float | 51 | nvoBlr2Stat | inc count (9) | Output (non-polled) |  | 30019/128
| 12-Boiler 3 Status | blr3stat_5 | ü | AV:48 | data float | 52 | nvoBlr3Stat | inc count (9) | Output (non-polled) |  | 30020/128
| 13-Boiler 4 Status | blr4stat_5 | ü | AV:1 | data float | 53 | nvoBlr4Stat | inc count (9) | Output (non-polled) |  | 30021/128
| 14-Boiler 5 Status | blr5stat_5 | ü | AV:2 | data float | 54 | nvoBlr5Stat | inc count (9) | Output (non-polled) |  | 30022/128
| 15-Boiler 6 Status | blr6stat_5 | ü | AV:3 | data float | 55 | nvoBlr6Stat | inc count (9) | Output (non-polled) |  | 30023/128
| 16-Boiler 7 Status | blr7stat_5 | ü | AV:4 | data float | 56 | nvoBlr7Stat | inc count (9) | Output (non-polled) |  | 30024/128
| 17-Boiler 8 Status | blr8stat_5 | ü | AV:5 | data float | 57 | nvoBlr8Stat | inc count (9) | Output (non-polled) |  | 30025/128
| 18-Net Blr 1 Status | blr9stat_5 | ü | AV:6 | data float | 58 | nvoNetBlr1Stat | inc count (9) | Output (non-polled) |  | 30026/128
| 19-Net Blr 2 Status | blr10stat_5 | ü | AV:7 | data float | 59 | nvoNetBlr2Stat | inc count (9) | Output (non-polled) |  | 30027/128
| 20-Net Blr 3 Status | blr11stat_5 | ü | AV:8 | data float | 60 | nvoNetBlr3Stat | inc count (9) | Output (non-polled) |  | 30028/128
| 21-Net Blr 4 Status | blr12stat_5 | ü | AV:9 | data float | 61 | nvoNetBlr4Stat | inc count (9) | Output (non-polled) |  | 30029/128

## 8 C-Mores-1 ACS
BACnet/IP, BACnet MS/TP, Metasys N2, and LonWorks Points List
8 C-Mores and 1 BMS
Equipment | Point Name | Name | Read Only |  | BACnet Type:ID | N2 Type | N2 ID | Lon SNVT NAME | Lon SNVT | Lon Direction | ModBus/Unit Address
Blr Addr 1
| 01-Fire Rate Out | boilerstate_1 | ü |  | AV:26 | data float | 1 | nvoBlrState1 | inc count (9) | Output (non-polled) | 30009/1
| 02-Active Setpoint | effectsetpt_1 | ü |  | AV:27 | data float | 2 | nvoEffSetpt1 | inc count (9) | Output (non-polled) | 30017/1
| 03-Net Remote Setpt | setpt_1 |  |  | AV:24 | data float | 3 | nviSetpt1 | inc count (9) | Input (non-polling) | 40001/1
| 05-Fire Rate In | boilerload_1 | ü |  | AV:28 | data float | 5 | nvoBlrLoad1 | inc count (9) | Output (non-polled) | 30018/1
| 06-Outlet Temp | localsuptemp_1 | ü |  | AV:29 | data float | 6 | nvoLocSupTmp1 | inc count (9) | Output (non-polled) | 30003/1
| 07-Display Code | dispcode_1 | ü |  | AV:22 | data float | 7 | nvoDispCode1 | inc count (9) | Output (non-polled) | 30001/1
| 08-Unit Status | unitstat_1 | ü |  | AV:23 | data float | 8 | nvoUnitStat1 | inc count (9) | Output (non-polled) | 30002/1
| 09-Run Cycles | runcycles_1 | ü |  | AV:42 | data float | 9 | nvoRunCycles1 | 51 | Output (non-polled) | 30012-30013/1
| 10-Run Hours | runhours_1 | ü |  | AV:43 | data float | 10 | nvoRunHours1 | 51 | Output (non-polled) | 30014-30015/1
Blr Addr 2
| 01-Fire Rate Out | boilerstate_2 | ü |  | AV:30 | data float | 11 | nvoBlrState2 | inc count (9) | Output (non-polled) | 30009/2
| 02-Active Setpoint | effectsetpt_2 | ü |  | AV:46 | data float | 12 | nvoEffSetpt2 | inc count (9) | Output (non-polled) | 30017/2
| 03-Net Remote Setpt | setpt_2 |  |  | AV:47 | data float | 13 | nviSetpt2 | inc count (9) | Input (non-polling) | 40001/2
| 05-Fire Rate In | boilerload_2 | ü |  | AV:50 | data float | 15 | nvoBlrLoad2 | inc count (9) | Output (non-polled) | 30018/2
| 06-Outlet Temp | localsuptemp_2 | ü |  | AV:51 | data float | 16 | nvoLocSupTmp2 | inc count (9) | Output (non-polled) | 30003/2
| 07-Display Code | dispcode_2 | ü |  | AV:52 | data float | 17 | nvoDispCode2 | inc count (9) | Output (non-polled) | 30001/2
| 08-Unit Status | unitstat_2 | ü |  | AV:53 | data float | 18 | nvoUnitStat2 | inc count (9) | Output (non-polled) | 30002/2
| 09-Run Cycles | runcycles_2 | ü |  | AV:44 | data float | 19 | nvoRunCycles2 | 51 | Output (non-polled) | 30012-30013/2
| 10-Run Hours | runhours_2 | ü |  | AV:45 | data float | 20 | nvoRunHours2 | 51 | Output (non-polled) | 30014-30015/2
Blr Addr 3
| 01-Fire Rate Out | boilerstate_3 | ü |  | AV:54 | data float | 21 | nvoBlrState3 | inc count (9) | Output (non-polled) | 30009/3
| 02-Active Setpoint | effectsetpt_3 | ü |  | AV:55 | data float | 22 | nvoEffSetpt3 | inc count (9) | Output (non-polled) | 30017/3
| 03-Net Remote Setpt | setpt_3 |  |  | AV:56 | data float | 23 | nviSetpt3 | inc count (9) | Input (non-polling) | 40001/3
| 05-Fire Rate In | boilerload_3 | ü |  | AV:60 | data float | 25 | nvoBlrLoad3 | inc count (9) | Output (non-polled) | 30018/3
| 06-Outlet Temp | localsuptemp_3 | ü |  | AV:61 | data float | 26 | nvoLocSupTmp3 | inc count (9) | Output (non-polled) | 30003/3
| 07-Display Code | dispcode_3 | ü |  | AV:62 | data float | 27 | nvoDispCode3 | inc count (9) | Output (non-polled) | 30001/3
| 08-Unit Status | unitstat_3 | ü |  | AV:63 | data float | 28 | nvoUnitStat3 | inc count (9) | Output (non-polled) | 30002/3
| 09-Run Cycles | runcycles_3 | ü |  | AV:58 | data float | 29 | nvoRunCycles3 | 51 | Output (non-polled) | 30012-30013/3
| 10-Run Hours | runhours_3 | ü |  | AV:59 | data float | 30 | nvoRunHours3 | 51 | Output (non-polled) | 30014-30015/3
Blr Addr 4
| 01-Fire Rate Out | boilerstate_4 | ü |  | AV:70 | data float | 31 | nvoBlrState4 | inc count (9) | Output (non-polled) | 30009/4
| 02-Active Setpoint | effectsetpt_4 | ü |  | AV:71 | data float | 32 | nvoEffSetpt4 | inc count (9) | Output (non-polled) | 30017/4
| 03-Net Remote Setpt | setpt_4 |  |  | AV:72 | data float | 33 | nviSetpt4 | inc count (9) | Input (non-polling) | 40001/4
| 05-Fire Rate In | boilerload_4 | ü |  | AV:73 | data float | 35 | nvoBlrLoad4 | inc count (9) | Output (non-polled) | 30018/4
| 06-Outlet Temp | localsuptemp_4 | ü |  | AV:65 | data float | 36 | nvoLocSupTmp4 | inc count (9) | Output (non-polled) | 30003/4
| 07-Display Code | dispcode_4 | ü |  | AV:66 | data float | 37 | nvoDispCode4 | inc count (9) | Output (non-polled) | 30001/4
| 08-Unit Status | unitstat_4 | ü |  | AV:67 | data float | 38 | nvoUnitStat4 | inc count (9) | Output (non-polled) | 30002/4
| 09-Run Cycles | runcycles_4 | ü |  | AV:68 | data float | 39 | nvoRunCycles4 | 51 | Output (non-polled) | 30012-30013/4
| 10-Run Hours | runhours_4 | ü |  | AV:69 | data float | 40 | nvoRunHours4 | 51 | Output (non-polled) | 30014-30015/4
Blr Addr 5
| 01-Fire Rate Out | boilerstate_5 | ü |  | AV:80 | data float | 41 | nvoBlrState5 | inc count (9) | Output (non-polled) | 30009/5
| 02-Active Setpoint | effectsetpt_5 | ü |  | AV:81 | data float | 42 | nvoEffSetpt5 | inc count (9) | Output (non-polled) | 30017/5
| 03-Net Remote Setpt | setpt_5 |  |  | AV:82 | data float | 43 | nviSetpt5 | inc count (9) | Input (non-polling) | 40001/5
| 05-Fire Rate In | boilerload_5 | ü |  | AV:74 | data float | 45 | nvoBlrLoad5 | inc count (9) | Output (non-polled) | 30018/5
| 06-Outlet Temp | localsuptemp_5 | ü |  | AV:75 | data float | 46 | nvoLocSupTmp5 | inc count (9) | Output (non-polled) | 30003/5
| 07-Display Code | dispcode_5 | ü |  | AV:76 | data float | 47 | nvoDispCode5 | inc count (9) | Output (non-polled) | 30001/5
| 08-Unit Status | unitstat_5 | ü |  | AV:77 | data float | 48 | nvoUnitStat5 | inc count (9) | Output (non-polled) | 30002/5
| 09-Run Cycles | runcycles_5 | ü |  | AV:78 | data float | 49 | nvoRunCycles5 | 51 | Output (non-polled) | 30012-30013/5
| 10-Run Hours | runhours_5 | ü |  | AV:79 | data float | 50 | nvoRunHours5 | 51 | Output (non-polled) | 30014-30015/5
Blr Addr 6
| 01-Fire Rate Out | boilerstate_6 |  | ü | AV:90 | data float | 51 | nvoBlrState6 | inc count (9) | Output (non-polled) | 30009/6
| 02-Active Setpoint | effectsetpt_6 |  | ü | AV:91 | data float | 52 | nvoEffSetpt6 | inc count (9) | Output (non-polled) | 30017/6
| 03-Net Remote Setpt | setpt_6 |  |  | AV:92 | data float | 53 | nviSetpt6 | inc count (9) | Input (non-polling) | 40001/6
| 05-Fire Rate In | boilerload_6 |  | ü | AV:84 | data float | 55 | nvoBlrLoad6 | inc count (9) | Output (non-polled) | 30018/6
| 06-Outlet Temp | localsuptemp_6 |  | ü | AV:85 | data float | 56 | nvoLocSupTmp6 | inc count (9) | Output (non-polled) | 30003/6
| 07-Display Code | dispcode_6 |  | ü | AV:86 | data float | 57 | nvoDispCode6 | inc count (9) | Output (non-polled) | 30001/6
| 08-Unit Status | unitstat_6 |  | ü | AV:87 | data float | 58 | nvoUnitStat6 | inc count (9) | Output (non-polled) | 30002/6
| 09-Run Cycles | runcycles_6 |  | ü | AV:88 | data float | 59 | nvoRunCycles6 | 51 | Output (non-polled) | 30012-30013/6
| 10-Run Hours | runhours_6 |  | ü | AV:89 | data float | 60 | nvoRunHours6 | 51 | Output (non-polled) | 30014-30015/6
Blr Addr 7
| 01-Fire Rate Out | boilerstate_7 |  | ü | AV:100 | data float | 61 | nvoBlrState7 | inc count (9) | Output (non-polled) | 30009/7
| 02-Active Setpoint | effectsetpt_7 |  | ü | AV:101 | data float | 62 | nvoEffSetpt7 | inc count (9) | Output (non-polled) | 30017/7
| 03-Net Remote Setpt | setpt_7 |  |  | AV:102 | data float | 63 | nviSetpt7 | inc count (9) | Input (non-polling) | 40001/7
| 05-Fire Rate In | boilerload_7 |  | ü | AV:94 | data float | 65 | nvoBlrLoad7 | inc count (9) | Output (non-polled) | 30018/7
| 06-Outlet Temp | localsuptemp_7 |  | ü | AV:95 | data float | 66 | nvoLocSupTmp7 | inc count (9) | Output (non-polled) | 30003/7
| 07-Display Code | dispcode_7 |  | ü | AV:96 | data float | 67 | nvoDispCode7 | inc count (9) | Output (non-polled) | 30001/7
| 08-Unit Status | unitstat_7 |  | ü | AV:97 | data float | 68 | nvoUnitStat7 | inc count (9) | Output (non-polled) | 30002/7
| 09-Run Cycles | runcycles_7 |  | ü | AV:98 | data float | 69 | nvoRunCycles7 | 51 | Output (non-polled) | 30012-30013/7
| 10-Run Hours | runhours_7 |  | ü | AV:99 | data float | 70 | nvoRunHours7 | 51 | Output (non-polled) | 30014-30015/7
Blr Addr 8
| 01-Fire Rate Out | boilerstate_8 |  | ü | AV:110 | data float | 71 | nvoBlrState8 | inc count (9) | Output (non-polled) | 30009/8
| 02-Active Setpoint | effectsetpt_8 |  | ü | AV:111 | data float | 72 | nvoEffSetpt8 | inc count (9) | Output (non-polled) | 30017/8
| 03-Net Remote Setpt | setpt_8 |  |  | AV:112 | data float | 73 | nviSetpt8 | inc count (9) | Input (non-polling) | 40001/8
| 05-Fire Rate In | boilerload_8 |  | ü | AV:104 | data float | 75 | nvoBlrLoad8 | inc count (9) | Output (non-polled) | 30018/8
| 06-Outlet Temp | localsuptemp_8 |  | ü | AV:105 | data float | 76 | nvoLocSupTmp8 | inc count (9) | Output (non-polled) | 30003/8
| 07-Display Code | dispcode_8 |  | ü | AV:106 | data float | 77 | nvoDispCode8 | inc count (9) | Output (non-polled) | 30001/8
| 08-Unit Status | unitstat_8 |  | ü | AV:107 | data float | 78 | nvoUnitStat8 | inc count (9) | Output (non-polled) | 30002/8
| 09-Run Cycles | runcycles_8 |  | ü | AV:108 | data float | 79 | nvoRunCycles8 | 51 | Output (non-polled) | 30012-30013/8
| 10-Run Hours | runhours_8 |  | ü | AV:109 | data float | 80 | nvoRunHours8 | 51 | Output (non-polled) | 30014-30015/8
BMS Addr 128
| 01-Fire Rate Out | boilerstate_13 |  | ü | AV:31 | data float | 121 | nvoBlrState | inc count (9) | Output (non-polled) | 30005/128
| 02-Header Set Temp | effectsetpt_13 |  | ü | AV:32 | data float | 122 | nvoEffSetpt | inc count (9) | Output (non-polled) | 30006/128
| 03-Net Header Set Temp | setpt_13 |  |  | AV:33 | data float | 123 | nviSetpt | inc count (9) | Input (non-polling) | 40005/128
| 04-Header Temp | localsuptemp_13 |  | ü | AV:34 | data float | 124 | nvoLocSupTmp | inc count (9) | Output (non-polled) | 30002/128
| 05-Outside Air Temp | localoatemp_13 |  | ü | AV:35 | data float | 125 | nvoLocOATmp | inc count (9) | Output (non-polled) | 30003/128
| 06-Display Code | dispcode_13 |  | ü | AV:36 | data float | 126 | nvoDispCode | inc count (9) | Output (non-polled) | 30011/128
| 07-Num Boilers Fired | blrfired_13 |  | ü | AV:37 | data float | 127 | nvoBlrsFired | inc count (9) | Output (non-polled) | 30008/128
| 08-Num Boilers Online | blronline_13 |  | ü | AV:38 | data float | 128 | nvoBlrsOnline | inc count (9) | Output (non-polled) | 30009/128
| 09-Last Blr Fired | blrlast_13 |  | ü | AV:39 | data float | 129 | nvoLastBlrFired | inc count (9) | Output (non-polled) | 30017/128
| 10-Boiler 1 Status | blr1stat_13 |  | ü | AV:40 | data float | 130 | nvoBlr1Stat | inc count (9) | Output (non-polled) | 30018/128
| 11-Boiler 2 Status | blr2stat_13 |  | ü | AV:41 | data float | 131 | nvoBlr2Stat | inc count (9) | Output (non-polled) | 30019/128
| 12-Boiler 3 Status | blr3stat_13 |  | ü | AV:48 | data float | 132 | nvoBlr3Stat | inc count (9) | Output (non-polled) | 30020/128
| 13-Boiler 4 Status | blr4stat_13 |  | ü | AV:1 | data float | 133 | nvoBlr4Stat | inc count (9) | Output (non-polled) | 30021/128
| 14-Boiler 5 Status | blr5stat_13 |  | ü | AV:2 | data float | 134 | nvoBlr5Stat | inc count (9) | Output (non-polled) | 30022/128
| 15-Boiler 6 Status | blr6stat_13 |  | ü | AV:3 | data float | 135 | nvoBlr6Stat | inc count (9) | Output (non-polled) | 30023/128
| 16-Boiler 7 Status | blr7stat_13 |  | ü | AV:4 | data float | 136 | nvoBlr7Stat | inc count (9) | Output (non-polled) | 30024/128
| 17-Boiler 8 Status | blr8stat_13 |  | ü | AV:5 | data float | 137 | nvoBlr8Stat | inc count (9) | Output (non-polled) | 30025/128
| 18-Net Blr 1 Status | blr9stat_13 |  | ü | AV:6 | data float | 138 | nvoNetBlr1Stat | inc count (9) | Output (non-polled) | 30026/128
| 19-Net Blr 2 Status | blr10stat_13 |  | ü | AV:7 | data float | 139 | nvoNetBlr2Stat | inc count (9) | Output (non-polled) | 30027/128
| 20-Net Blr 3 Status | blr11stat_13 |  | ü | AV:8 | data float | 140 | nvoNetBlr3Stat | inc count (9) | Output (non-polled) | 30028/128
| 21-Net Blr 4 Status | blr12stat_13 |  | ü | AV:9 | data float | 141 | nvoNetBlr4Stat | inc count (9) | Output (non-polled) | 30029/128
| 22-Net Blr 5 Status | blr13stat_13 |  | ü | AV:10 | data float | 142 | nvoNetBlr5Stat | inc count (9) | Output (non-polled) | 30030/128
| 23-Net Blr 6 Status | blr14stat_13 |  | ü | AV:11 | data float | 143 | nvoNetBlr6Stat | inc count (9) | Output (non-polled) | 30031/128
| 24-Net Blr 7 Status | blr15stat_13 |  | ü | AV:12 | data float | 144 | nvoNetBlr7Stat | inc count (9) | Output (non-polled) | 30032/128
| 25-Net Blr 8 Status | blr16stat_13 |  | ü | AV:13 | data float | 145 | nvoNetBlr8Stat | inc count (9) | Output (non-polled) | 30033/128

## 12 C-Mores-1 ACS
BACnet/IP, BACnet MS/TP, Metasys N2, and LonWorks Points List
12 C-Mores and 1 BMS
Equipment | Point Name | Name | Read Only | BACnet Type:ID | N2 Type | N2 ID | Lon SNVT NAME | Lon SNVT | Lon Direction | ModBus/Unit Address
Blr Addr 1
| 01-Fire Rate Out | boilerstate_1 | ü | AV:26 | data float | 1 | nvoBlrState1 | inc count (9) | Output (non-polled) | 30009/1
| 02-Active Setpoint | effectsetpt_1 | ü | AV:27 | data float | 2 | nvoEffSetpt1 | inc count (9) | Output (non-polled) | 30017/1
| 03-Net Remote Setpt | setpt_1 |  | AV:24 | data float | 3 | nviSetpt1 | inc count (9) | Input (non-polling) | 40001/1
| 05-Fire Rate In | boilerload_1 | ü | AV:28 | data float | 5 | nvoBlrLoad1 | inc count (9) | Output (non-polled) | 30018/1
| 06-Outlet Temp | localsuptemp_1 | ü | AV:29 | data float | 6 | nvoLocSupTmp1 | inc count (9) | Output (non-polled) | 30003/1
| 07-Display Code | dispcode_1 | ü | AV:22 | data float | 7 | nvoDispCode1 | inc count (9) | Output (non-polled) | 30001/1
| 08-Unit Status | unitstat_1 | ü | AV:23 | data float | 8 | nvoUnitStat1 | inc count (9) | Output (non-polled) | 30002/1
| 09-Run Cycles | runcycles_1 | ü | AV:42 | data float | 9 | nvoRunCycles1 | 51 | Output (non-polled) | 30012-30013/1
| 10-Run Hours | runhours_1 | ü | AV:43 | data float | 10 | nvoRunHours1 | 51 | Output (non-polled) | 30014-30015/1
Blr Addr 2
| 01-Fire Rate Out | boilerstate_2 | ü | AV:30 | data float | 11 | nvoBlrState2 | inc count (9) | Output (non-polled) | 30009/2
| 02-Active Setpoint | effectsetpt_2 | ü | AV:46 | data float | 12 | nvoEffSetpt2 | inc count (9) | Output (non-polled) | 30017/2
| 03-Net Remote Setpt | setpt_2 |  | AV:47 | data float | 13 | nviSetpt2 | inc count (9) | Input (non-polling) | 40001/2
| 05-Fire Rate In | boilerload_2 | ü | AV:50 | data float | 15 | nvoBlrLoad2 | inc count (9) | Output (non-polled) | 30018/2
| 06-Outlet Temp | localsuptemp_2 | ü | AV:51 | data float | 16 | nvoLocSupTmp2 | inc count (9) | Output (non-polled) | 30003/2
| 07-Display Code | dispcode_2 | ü | AV:52 | data float | 17 | nvoDispCode2 | inc count (9) | Output (non-polled) | 30001/2
| 08-Unit Status | unitstat_2 | ü | AV:53 | data float | 18 | nvoUnitStat2 | inc count (9) | Output (non-polled) | 30002/2
| 09-Run Cycles | runcycles_2 | ü | AV:44 | data float | 19 | nvoRunCycles2 | 51 | Output (non-polled) | 30012-30013/2
| 10-Run Hours | runhours_2 | ü | AV:45 | data float | 20 | nvoRunHours2 | 51 | Output (non-polled) | 30014-30015/2
Blr Addr 3
| 01-Fire Rate Out | boilerstate_3 | ü | AV:54 | data float | 21 | nvoBlrState3 | inc count (9) | Output (non-polled) | 30009/3
| 02-Active Setpoint | effectsetpt_3 | ü | AV:55 | data float | 22 | nvoEffSetpt3 | inc count (9) | Output (non-polled) | 30017/3
| 03-Net Remote Setpt | setpt_3 |  | AV:56 | data float | 23 | nviSetpt3 | inc count (9) | Input (non-polling) | 40001/3
| 05-Fire Rate In | boilerload_3 | ü | AV:60 | data float | 25 | nvoBlrLoad3 | inc count (9) | Output (non-polled) | 30018/3
| 06-Outlet Temp | localsuptemp_3 | ü | AV:61 | data float | 26 | nvoLocSupTmp3 | inc count (9) | Output (non-polled) | 30003/3
| 07-Display Code | dispcode_3 | ü | AV:62 | data float | 27 | nvoDispCode3 | inc count (9) | Output (non-polled) | 30001/3
| 08-Unit Status | unitstat_3 | ü | AV:63 | data float | 28 | nvoUnitStat3 | inc count (9) | Output (non-polled) | 30002/3
| 09-Run Cycles | runcycles_3 | ü | AV:58 | data float | 29 | nvoRunCycles3 | 51 | Output (non-polled) | 30012-30013/3
| 10-Run Hours | runhours_3 | ü | AV:59 | data float | 30 | nvoRunHours3 | 51 | Output (non-polled)
30014-30015/3
Blr Addr 4
| 01-Fire Rate Out | boilerstate_4 | ü | AV:70 | data float | 31 | nvoBlrState4 | inc count (9) | Output (non-polled) | 30009/4
| 02-Active Setpoint | effectsetpt_4 | ü | AV:71 | data float | 32 | nvoEffSetpt4 | inc count (9) | Output (non-polled) | 30017/4
| 03-Net Remote Setpt | setpt_4 |  | AV:72 | data float | 33 | nviSetpt4 | inc count (9) | Input (non-polling) | 40001/4
| 05-Fire Rate In | boilerload_4 | ü | AV:73 | data float | 35 | nvoBlrLoad4 | inc count (9) | Output (non-polled) | 30018/4
| 06-Outlet Temp | localsuptemp_4 | ü | AV:65 | data float | 36 | nvoLocSupTmp4 | inc count (9) | Output (non-polled) | 30003/4
| 07-Display Code | dispcode_4 | ü | AV:66 | data float | 37 | nvoDispCode4 | inc count (9) | Output (non-polled) | 30001/4
| 08-Unit Status | unitstat_4 | ü | AV:67 | data float | 38 | nvoUnitStat4 | inc count (9) | Output (non-polled) | 30002/4
| 09-Run Cycles | runcycles_4 | ü | AV:68 | data float | 39 | nvoRunCycles4 | 51 | Output (non-polled) | 30012-30013/4
| 10-Run Hours | runhours_4 | ü | AV:69 | data float | 40 | nvoRunHours4 | 51 | Output (non-polled) | 30014-30015/4
Blr Addr 5
| 01-Fire Rate Out | boilerstate_5 | ü | AV:80 | data float | 41 | nvoBlrState5 | inc count (9) | Output (non-polled) | 30009/5
| 02-Active Setpoint | effectsetpt_5 | ü | AV:81 | data float | 42 | nvoEffSetpt5 | inc count (9) | Output (non-polled) | 30017/5
| 03-Net Remote Setpt | setpt_5 |  | AV:82 | data float | 43 | nviSetpt5 | inc count (9) | Input (non-polling) | 40001/5
| 05-Fire Rate In | boilerload_5 | ü | AV:74 | data float | 45 | nvoBlrLoad5 | inc count (9) | Output (non-polled) | 30018/5
| 06-Outlet Temp | localsuptemp_5 | ü | AV:75 | data float | 46 | nvoLocSupTmp5 | inc count (9) | Output (non-polled) | 30003/5
| 07-Display Code | dispcode_5 | ü | AV:76 | data float | 47 | nvoDispCode5 | inc count (9) | Output (non-polled) | 30001/5
| 08-Unit Status | unitstat_5 | ü | AV:77 | data float | 48 | nvoUnitStat5 | inc count (9) | Output (non-polled) | 30002/5
| 09-Run Cycles | runcycles_5 | ü | AV:78 | data float | 49 | nvoRunCycles5 | 51 | Output (non-polled) | 30012-30013/5
| 10-Run Hours | runhours_5 | ü | AV:79 | data float | 50 | nvoRunHours5 | 51 | Output (non-polled) | 30014-30015/5
Blr Addr 6
| 01-Fire Rate Out | boilerstate_6 | ü | AV:90 | data float | 51 | nvoBlrState6 | inc count (9) | Output (non-polled) | 30009/6
| 02-Active Setpoint | effectsetpt_6 | ü | AV:91 | data float | 52 | nvoEffSetpt6 | inc count (9) | Output (non-polled) | 30017/6
| 03-Net Remote Setpt | setpt_6 |  | AV:92 | data float | 53 | nviSetpt6 | inc count (9) | Input (non-polling) | 40001/6
| 05-Fire Rate In | boilerload_6 | ü | AV:84 | data float | 55 | nvoBlrLoad6 | inc count (9) | Output (non-polled) | 30018/6
| 06-Outlet Temp | localsuptemp_6 | ü | AV:85 | data float | 56 | nvoLocSupTmp6 | inc count (9) | Output (non-polled) | 30003/6
| 07-Display Code | dispcode_6 | ü | AV:86 | data float | 57 | nvoDispCode6 | inc count (9) | Output (non-polled) | 30001/6
| 08-Unit Status | unitstat_6 | ü | AV:87 | data float | 58 | nvoUnitStat6 | inc count (9) | Output (non-polled) | 30002/6
| 09-Run Cycles | runcycles_6 | ü | AV:88 | data float | 59 | nvoRunCycles6 | 51 | Output (non-polled) | 30012-30013/6
| 10-Run Hours | runhours_6 | ü | AV:89 | data float | 60 | nvoRunHours6 | 51 | Output (non-polled)
30014-30015/6
Blr Addr 7
| 01-Fire Rate Out | boilerstate_7 | ü | AV:100 | data float | 61 | nvoBlrState7 | inc count (9) | Output (non-polled) | 30009/7
| 02-Active Setpoint | effectsetpt_7 | ü | AV:101 | data float | 62 | nvoEffSetpt7 | inc count (9) | Output (non-polled) | 30017/7
| 03-Net Remote Setpt | setpt_7 |  | AV:102 | data float | 63 | nviSetpt7 | inc count (9) | Input (non-polling) | 40001/7
| 05-Fire Rate In | boilerload_7 | ü | AV:94 | data float | 65 | nvoBlrLoad7 | inc count (9) | Output (non-polled) | 30018/7
| 06-Outlet Temp | localsuptemp_7 | ü | AV:95 | data float | 66 | nvoLocSupTmp7 | inc count (9) | Output (non-polled) | 30003/7
| 07-Display Code | dispcode_7 | ü | AV:96 | data float | 67 | nvoDispCode7 | inc count (9) | Output (non-polled) | 30001/7
| 08-Unit Status | unitstat_7 | ü | AV:97 | data float | 68 | nvoUnitStat7 | inc count (9) | Output (non-polled) | 30002/7
| 09-Run Cycles | runcycles_7 | ü | AV:98 | data float | 69 | nvoRunCycles7 | 51 | Output (non-polled) | 30012-30013/7
| 10-Run Hours | runhours_7 | ü | AV:99 | data float | 70 | nvoRunHours7 | 51 | Output (non-polled) | 30014-30015/7
Blr Addr 8
| 01-Fire Rate Out | boilerstate_8 | ü | AV:110 | data float | 71 | nvoBlrState8 | inc count (9) | Output (non-polled) | 30009/8
| 02-Active Setpoint | effectsetpt_8 | ü | AV:111 | data float | 72 | nvoEffSetpt8 | inc count (9) | Output (non-polled) | 30017/8
| 03-Net Remote Setpt | setpt_8 |  | AV:112 | data float | 73 | nviSetpt8 | inc count (9) | Input (non-polling) | 40001/8
| 05-Fire Rate In | boilerload_8 | ü | AV:104 | data float | 75 | nvoBlrLoad8 | inc count (9) | Output (non-polled) | 30018/8
| 06-Outlet Temp | localsuptemp_8 | ü | AV:105 | data float | 76 | nvoLocSupTmp8 | inc count (9) | Output (non-polled) | 30003/8
| 07-Display Code | dispcode_8 | ü | AV:106 | data float | 77 | nvoDispCode8 | inc count (9) | Output (non-polled) | 30001/8
| 08-Unit Status | unitstat_8 | ü | AV:107 | data float | 78 | nvoUnitStat8 | inc count (9) | Output (non-polled) | 30002/8
| 09-Run Cycles | runcycles_8 | ü | AV:108 | data float | 79 | nvoRunCycles8 | 51 | Output (non-polled) | 30012-30013/8
| 10-Run Hours | runhours_8 | ü | AV:109 | data float | 80 | nvoRunHours8 | 51 | Output (non-polled) | 30014-30015/8
Blr Addr 9
| 01-Fire Rate Out | boilerstate_9 | ü | AV:120 | data float | 81 | nvoBlrState9 | inc count (9) | Output (non-polled) | 30009/9
| 02-Active Setpoint | effectsetpt_9 | ü | AV:121 | data float | 82 | nvoEffSetpt9 | inc count (9) | Output (non-polled) | 30017/9
| 03-Net Remote Setpt | setpt_9 |  | AV:122 | data float | 83 | nviSetpt9 | inc count (9) | Input (non-polling) | 40001/9
| 05-Fire Rate In | boilerload_9 | ü | AV:114 | data float | 85 | nvoBlrLoad9 | inc count (9) | Output (non-polled) | 30018/9
| 06-Outlet Temp | localsuptemp_9 | ü | AV:115 | data float | 86 | nvoLocSupTmp9 | inc count (9) | Output (non-polled) | 30003/9
| 07-Display Code | dispcode_9 | ü | AV:116 | data float | 87 | nvoDispCode9 | inc count (9) | Output (non-polled) | 30001/9
| 08-Unit Status | unitstat_9 | ü | AV:117 | data float | 88 | nvoUnitStat9 | inc count (9) | Output (non-polled) | 30002/9
| 09-Run Cycles | runcycles_9 | ü | AV:118 | data float | 89 | nvoRunCycles9 | 51 | Output (non-polled) | 30012-30013/9
| 10-Run Hours | runhours_9 | ü | AV:119 | data float | 90 | nvoRunHours9 | 51 | Output (non-polled)
30014-30015/9
Blr Addr 10
| 01-Fire Rate Out | boilerstate_10 | ü | AV:130 | data float | 91 | nvoBlrState10 | inc count (9) | Output (non-polled) | 30009/10
| 02-Active Setpoint | effectsetpt_10 | ü | AV:131 | data float | 92 | nvoEffSetpt10 | inc count (9) | Output (non-polled) | 30017/10
| 03-Net Remote Setpt | setpt_10 |  | AV:132 | data float | 93 | nviSetpt10 | inc count (9) | Input (non-polling) | 40001/10
| 05-Fire Rate In | boilerload_10 | ü | AV:124 | data float | 95 | nvoBlrLoad10 | inc count (9) | Output (non-polled) | 30018/10
| 06-Outlet Temp | localsuptemp_10 | ü | AV:125 | data float | 96 | nvoLocSupTmp10 | inc count (9) | Output (non-polled) | 30003/10
| 07-Display Code | dispcode_10 | ü | AV:126 | data float | 97 | nvoDispCode10 | inc count (9) | Output (non-polled) | 30001/10
| 08-Unit Status | unitstat_10 | ü | AV:127 | data float | 98 | nvoUnitStat10 | inc count (9) | Output (non-polled) | 30002/10
| 09-Run Cycles | runcycles_10 | ü | AV:128 | data float | 99 | nvoRunCycles10 | 51 | Output (non-polled) | 30012-30013/10
| 10-Run Hours | runhours_10 | ü | AV:129 | data float | 100 | nvoRunHours10 | 51 | Output (non-polled) | 30014-30015/10
Blr Addr 11
| 01-Fire Rate Out | boilerstate_11 | ü | AV:140 | data float | 101 | nvoBlrState11 | inc count (9) | Output (non-polled) | 30009/11
| 02-Active Setpoint | effectsetpt_11 | ü | AV:141 | data float | 102 | nvoEffSetpt11 | inc count (9) | Output (non-polled) | 30017/11
| 03-Net Remote Setpt | setpt_11 |  | AV:142 | data float | 103 | nviSetpt11 | inc count (9) | Input (non-polling) | 40001/11
| 05-Fire Rate In | boilerload_11 | ü | AV:134 | data float | 105 | nvoBlrLoad11 | inc count (9) | Output (non-polled) | 30018/11
| 06-Outlet Temp | localsuptemp_11 | ü | AV:135 | data float | 106 | nvoLocSupTmp11 | inc count (9) | Output (non-polled) | 30003/11
| 07-Display Code | dispcode_11 | ü | AV:136 | data float | 107 | nvoDispCode11 | inc count (9) | Output (non-polled) | 30001/11
| 08-Unit Status | unitstat_11 | ü | AV:137 | data float | 108 | nvoUnitStat11 | inc count (9) | Output (non-polled) | 30002/11
| 09-Run Cycles | runcycles_11 | ü | AV:138 | data float | 109 | nvoRunCycles11 | 51 | Output (non-polled) | 30012-30013/11
| 10-Run Hours | runhours_11 | ü | AV:139 | data float | 110 | nvoRunHours11 | 51 | Output (non-polled) | 30014-30015/11
Blr Addr 12
| 01-Fire Rate Out | boilerstate_12 | ü | AV:150 | data float | 111 | nvoBlrState12 | inc count (9) | Output (non-polled) | 30009/12
| 02-Active Setpoint | effectsetpt_12 | ü | AV:151 | data float | 112 | nvoEffSetpt12 | inc count (9) | Output (non-polled) | 30017/12
| 03-Net Remote Setpt | setpt_12 |  | AV:152 | data float | 113 | nviSetpt12 | inc count (9) | Input (non-polling) | 40001/12
| 05-Fire Rate In | boilerload_12 | ü | AV:144 | data float | 115 | nvoBlrLoad12 | inc count (9) | Output (non-polled) | 30018/12
| 06-Outlet Temp | localsuptemp_12 | ü | AV:145 | data float | 116 | nvoLocSupTmp12 | inc count (9) | Output (non-polled) | 30003/12
| 07-Display Code | dispcode_12 | ü | AV:146 | data float | 117 | nvoDispCode12 | inc count (9) | Output (non-polled) | 30001/12
| 08-Unit Status | unitstat_12 | ü | AV:147 | data float | 118 | nvoUnitStat12 | inc count (9) | Output (non-polled) | 30002/12
| 09-Run Cycles | runcycles_12 | ü | AV:148 | data float | 119 | nvoRunCycles12 | 51 | Output (non-polled) | 30012-30013/12
| 10-Run Hours | runhours_12 | ü | AV:149 | data float | 120 | nvoRunHours12 | 51 | Output (non-polled)
30014-30015/12
BMS Addr 128
| 01-Fire Rate Out | boilerstate_13 | ü | AV:31 | data float | 121 | nvoBlrState | inc count (9) | Output (non-polled) | 30005/128
| 02-Header Set Temp | effectsetpt_13 | ü | AV:32 | data float | 122 | nvoEffSetpt | inc count (9) | Output (non-polled) | 30006/128
| 03-Net Header Set Temp | setpt_13 |  | AV:33 | data float | 123 | nviSetpt | inc count (9) | Input (non-polling) | 40005/128
| 04-Header Temp | localsuptemp_13 | ü | AV:34 | data float | 124 | nvoLocSupTmp | inc count (9) | Output (non-polled) | 30002/128
| 05-Outside Air Temp | localoatemp_13 | ü | AV:35 | data float | 125 | nvoLocOATmp | inc count (9) | Output (non-polled) | 30003/128
| 06-Display Code | dispcode_13 | ü | AV:36 | data float | 126 | nvoDispCode | inc count (9) | Output (non-polled) | 30011/128
| 07-Num Boilers Fired | blrfired_13 | ü | AV:37 | data float | 127 | nvoBlrsFired | inc count (9) | Output (non-polled) | 30008/128
| 08-Num Boilers Online | blronline_13 | ü | AV:38 | data float | 128 | nvoBlrsOnline | inc count (9) | Output (non-polled) | 30009/128
| 09-Last Blr Fired | blrlast_13 | ü | AV:39 | data float | 129 | nvoLastBlrFired | inc count (9) | Output (non-polled) | 30017/128
| 10-Boiler 1 Status | blr1stat_13 | ü | AV:40 | data float | 130 | nvoBlr1Stat | inc count (9) | Output (non-polled) | 30018/128
| 11-Boiler 2 Status | blr2stat_13 | ü | AV:41 | data float | 131 | nvoBlr2Stat | inc count (9) | Output (non-polled) | 30019/128
| 12-Boiler 3 Status | blr3stat_13 | ü | AV:48 | data float | 132 | nvoBlr3Stat | inc count (9) | Output (non-polled) | 30020/128
| 13-Boiler 4 Status | blr4stat_13 | ü | AV:1 | data float | 133 | nvoBlr4Stat | inc count (9) | Output (non-polled) | 30021/128
| 14-Boiler 5 Status | blr5stat_13 | ü | AV:2 | data float | 134 | nvoBlr5Stat | inc count (9) | Output (non-polled) | 30022/128
| 15-Boiler 6 Status | blr6stat_13 | ü | AV:3 | data float | 135 | nvoBlr6Stat | inc count (9) | Output (non-polled) | 30023/128
| 16-Boiler 7 Status | blr7stat_13 | ü | AV:4 | data float | 136 | nvoBlr7Stat | inc count (9) | Output (non-polled) | 30024/128
| 17-Boiler 8 Status | blr8stat_13 | ü | AV:5 | data float | 137 | nvoBlr8Stat | inc count (9) | Output (non-polled) | 30025/128
| 18-Net Blr 1 Status | blr9stat_13 | ü | AV:6 | data float | 138 | nvoNetBlr1Stat | inc count (9) | Output (non-polled) | 30026/128
| 19-Net Blr 2 Status | blr10stat_13 | ü | AV:7 | data float | 139 | nvoNetBlr2Stat | inc count (9) | Output (non-polled) | 30027/128
| 20-Net Blr 3 Status | blr11stat_13 | ü | AV:8 | data float | 140 | nvoNetBlr3Stat | inc count (9) | Output (non-polled) | 30028/128
| 21-Net Blr 4 Status | blr12stat_13 | ü | AV:9 | data float | 141 | nvoNetBlr4Stat | inc count (9) | Output (non-polled) | 30029/128
| 22-Net Blr 5 Status | blr13stat_13 | ü | AV:10 | data float | 142 | nvoNetBlr5Stat | inc count (9) | Output (non-polled) | 30030/128
| 23-Net Blr 6 Status | blr14stat_13 | ü | AV:11 | data float | 143 | nvoNetBlr6Stat | inc count (9) | Output (non-polled) | 30031/128
| 24-Net Blr 7 Status | blr15stat_13 | ü | AV:12 | data float | 144 | nvoNetBlr7Stat | inc count (9) | Output (non-polled) | 30032/128
| 25-Net Blr 8 Status | blr16stat_13 | ü | AV:13 | data float | 145 | nvoNetBlr8Stat | inc count (9) | Output (non-polled) | 30033/128
| 26-Net Blr 9 Status | blr17stat_13 | ü | AV:14 | data float | 146 | nvoNetBlr9Stat | inc count (9) | Output (non-polled) | 30034/128
| 27-Net Blr 10 Status | blr18stat_13 | ü | AV:15 | data float | 147 | nvoNetBlr10Stat | inc count (9) | Output (non-polled) | 30035/128
| 28-Net Blr 11 Status | blr19stat_13 | ü | AV:16 | data float | 148 | nvoNetBlr11Stat | inc count (9) | Output (non-polled) | 30036/128
| 29-Net Blr 12 Status | blr20stat_13 | ü | AV:17 | data float | 149 | nvoNetBlr12Stat | inc count (9) | Output (non-polled) | 30037/128

## 4 MLX -ACS
BACnet/IP, BACnet MS/TP, Metasys N2, and LonWorks Points List
MLX and 1 BMS II
Equipment | Point Name | Name | Read Only | BACnet Type:ID | N2 Type | N2 ID | Lon SNVT NAME | Lon SNVT | Lon Direction | ModBus/Unit Address
BMS Addr 128
| 01-Fire Rate Out | boilerstate_5 | ü | AV:31 | data float | 41 | nvoBlrState | inc count (9) | Output (non-polled) | 30005/128
| 02-Header Set Temp | effectsetpt_5 | ü | AV:32 | data float | 42 | nvoEffSetpt | inc count (9) | Output (non-polled) | 30006/128
| 03-Net Header Set Temp | setpt_5 |  | AV:33 | data float | 43 | nviSetpt | inc count (9) | Input (non-polling) | 40005/128
| 04-Header Temp | localsuptemp_5 | ü | AV:34 | data float | 44 | nvoLocSupTmp | inc count (9) | Output (non-polled) | 30002/128
| 05-Outside Air Temp | localoatemp_5 | ü | AV:35 | data float | 45 | nvoLocOATmp | inc count (9) | Output (non-polled) | 30003/128
| 06-Display Code | dispcode_5 | ü | AV:36 | data float | 46 | nvoDispCode | inc count (9) | Output (non-polled) | 30011/128
| 07-Num Boilers Fired | blrfired_5 | ü | AV:37 | data float | 47 | nvoBlrsFired | inc count (9) | Output (non-polled) | 30008/128
| 08-Num Boilers Online | blronline_5 | ü | AV:38 | data float | 48 | nvoBlrsOnline | inc count (9) | Output (non-polled) | 30009/128
| 09-Last Blr Fired | blrlast_5 | ü | AV:39 | data float | 49 | nvoLastBlrFired | inc count (9) | Output (non-polled) | 30017/128
| 18-Net Blr 1 Status | blr9stat_5 | ü | AV:26 | data float | 58 | nvoNetBlr1Stat | inc count (9) | Output (non-polled) | 30026/128
| 19-Net Blr 2 Status | blr10stat_5 | ü | AV:27 | data float | 59 | nvoNetBlr2Stat | inc count (9) | Output (non-polled) | 30027/128
| 20-Net Blr 3 Status | blr11stat_5 | ü | AV:47 | data float | 60 | nvoNetBlr3Stat | inc count (9) | Output (non-polled) | 30028/128
| 21-Net Blr 4 Status | blr12stat_5 | ü | AV:49 | data float | 61 | nvoNetBlr4Stat | inc count (9) | Output (non-polled) | 30029/128
Mlx Addr 1
| 01-Act Mod Lev | boilerstate_1 | ü | AV:134 | data float | 62 | nvoMlxState1 | inc count (9) | Output (non-polled) | 41009/1
| 02-Target Setpoint | effectsetpt_1 | ü | AV:135 | data float | 63 | nvoMlxSetpt1 | inc count (9) | Output (non-polled) | 41019/1
| 03-Req Outlet Temp | setpt_1 |  | AV:136 | data float | 64 | nviMlxSetptRq1 | inc count (9) | Input (non-polling) | 41005/1
| 04-Net Direct Drive | boilercmd_1 |  | AV:137 | data float | 65 | nviMlxCmd1 | inc count (9) | Input (non-polling) | 40002/1
| 05-Mod Lev In | boilerload_1 | ü | AV:138 | data float | 66 | nvoMlxLoad1 | inc count (9) | Output (non-polled) | 41201/1
| 06-Flow Sens Temp | localsuptemp_1 | ü | AV:139 | data float | 67 | nvoMlxSupTmp1 | inc count (9) | Output (non-polled) | 41003/1
| 07-Display Code | dispcode_1 | ü | AV:140 | data float | 68 | nvoMlxDispCode1 | inc count (9) | Output (non-polled) | 30001/1
| 11-Error Code | errcode_1 | ü | AV:1 | data float | 69 | nvoMlxErrCode1 | 51 | Output (non-polled) | 40001/1
| 08-Unit Status | unitstat_1 | ü | AV:141 | data float | 150 | nvoMlxStat1 | inc count (9) | Output (non-polled) | 30002/1
| 09-Ret Flow Temp | returntemp_1 | ü | AV:2 | data float | 151 | nvoMlxRetTmp1 | inc count (9) | Output (non-polled) | 41004/1
Mlx Addr 2
| 01-Act Mod Lev | boilerstate_2 | ü | AV:144 | data float | 153 | nvoMlxState2 | inc count (9) | Output (non-polled) | 41009/2
| 02-Target Setpoint | effectsetpt_2 | ü | AV:145 | data float | 154 | nvoMlxSetpt2 | inc count (9) | Output (non-polled) | 41019/2
| 03-Req Outlet Temp | setpt_2 |  | AV:146 | data float | 155 | nviMlxSetptRq2 | inc count (9) | Input (non-polling) | 41005/2
| 04-Net Direct Drive | boilercmd_2 |  | AV:147 | data float | 156 | nviMlxCmd2 | inc count (9) | Input (non-polling) | 40002/2
| 05-Mod Lev In | boilerload_2 | ü | AV:148 | data float | 157 | nvoMlxLoad2 | inc count (9) | Output (non-polled) | 41201/2
| 06-Flow Sens Temp | localsuptemp_2 | ü | AV:149 | data float | 158 | nvoMlxSupTmp2 | inc count (9) | Output (non-polled) | 41003/2
| 07-Display Code | dispcode_2 | ü | AV:150 | data float | 159 | nvoMlxDispCode2 | inc count (9) | Output (non-polled) | 30001/2
| 11-Error Code | errcode_2 | ü | AV:4 | data float | 160 | nvoMlxErrCode2 | 51 | Output (non-polled) | 40001/2
| 08-Unit Status | unitstat_2 | ü | AV:151 | data float | 161 | nvoMlxStat2 | inc count (9) | Output (non-polled) | 30002/2
| 09-Ret Flow Temp | returntemp_2 | ü | AV:5 | data float | 162 | nvoMlxRetTmp2 | inc count (9) | Output (non-polled) | 41004/2
Mlx Addr 3
| 01-Act Mod Lev | boilerstate_3 | ü | AV:18 | data float | 164 | nvoMlxState3 | inc count (9) | Output (non-polled) | 41009/3
| 02-Target Setpoint | effectsetpt_3 | ü | AV:19 | data float | 165 | nvoMlxSetpt3 | inc count (9) | Output (non-polled) | 41019/3
| 03-Req Outlet Temp | setpt_3 |  | AV:20 | data float | 166 | nviMlxSetptRq3 | inc count (9) | Input (non-polling) | 41005/3
| 04-Net Direct Drive | boilercmd_3 |  | AV:21 | data float | 167 | nviMlxCmd3 | inc count (9) | Input (non-polling) | 40002/3
| 05-Mod Lev In | boilerload_3 | ü | AV:22 | data float | 168 | nvoMlxLoad3 | inc count (9) | Output (non-polled) | 41201/3
| 06-Flow Sens Temp | localsuptemp_3 | ü | AV:23 | data float | 169 | nvoMlxSupTmp3 | inc count (9) | Output (non-polled) | 41003/3
| 07-Display Code | dispcode_3 | ü | AV:24 | data float | 170 | nvoMlxDispCode3 | inc count (9) | Output (non-polled) | 30001/3
| 11-Error Code | errcode_3 | ü | AV:7 | data float | 171 | nvoMlxErrCode3 | 51 | Output (non-polled) | 40001/3
| 08-Unit Status | unitstat_3 | ü | AV:25 | data float | 172 | nvoMlxStat3 | inc count (9) | Output (non-polled) | 30002/3
| 09-Ret Flow Temp | returntemp_3 | ü | AV:8 | data float | 173 | nvoMlxRetTmp3 | inc count (9) | Output (non-polled) | 41004/3
Mlx Addr 4
| 01-Act Mod Lev | boilerstate_4 | ü | AV:28 | data float | 175 | nvoMlxState4 | inc count (9) | Output (non-polled) | 41009/4
| 02-Target Setpoint | effectsetpt_4 | ü | AV:29 | data float | 176 | nvoMlxSetpt4 | inc count (9) | Output (non-polled) | 41019/4
| 03-Req Outlet Temp | setpt_4 |  | AV:30 | data float | 177 | nviMlxSetptRq4 | inc count (9) | Input (non-polling) | 41005/4
| 04-Net Direct Drive | boilercmd_4 |  | AV:42 | data float | 178 | nviMlxCmd4 | inc count (9) | Input (non-polling) | 40002/4
| 05-Mod Lev In | boilerload_4 | ü | AV:43 | data float | 179 | nvoMlxLoad4 | inc count (9) | Output (non-polled) | 41201/4
| 06-Flow Sens Temp | localsuptemp_4 | ü | AV:44 | data float | 180 | nvoMlxSupTmp4 | inc count (9) | Output (non-polled) | 41003/4
| 07-Display Code | dispcode_4 | ü | AV:45 | data float | 181 | nvoMlxDispCode4 | inc count (9) | Output (non-polled) | 30001/4
| 11-Error Code | errcode_4 | ü | AV:10 | data float | 182 | nvoMlxErrCode4 | 51 | Output (non-polled) | 40001/4
| 08-Unit Status | unitstat_4 | ü | AV:46 | data float | 183 | nvoMlxStat4 | inc count (9) | Output (non-polled) | 30002/4
| 09-Ret Flow Temp | returntemp_4 | ü | AV:11 | data float | 184 | nvoMlxRetTmp4 | inc count (9) | Output (non-polled)
41004/4

## 4 ECS - SP
BACnet/IP, BACnet MS/TP, Metasys N2, and LonWorks Points List
ECS System & Smartplate
Equipment | Point Name | Name | Read Only | BACnet Type:ID | N2 Type | N2 ID | Lon SNVT NAME | Lon SNVT | Lon Direction | ModBus/Unit Address
E Valve Addr 29
| 01-Cntl Output Signal | boilerstate_1 | ü | AV:11 | data float | 1 | nvoEcsState29 | inc count (9) | Output (non-polled) | 30004/29
| 02-Setpoint | effectsetpt_1 | ü | AV:80 | data float | 2 | nvoEcsSetpt29 | inc count (9) | Output (non-polled) | 30006/29
| 03-RmSetpt | rmsetpt_1 |  | AV:81 | data float | 3 | nviEcsSetptRq29 | inc count (9) | Input (non-polling) | 40027/29
| 04-Outlet Temp | localsuptemp_1 | ü | AV:84 | data float | 4 | nvoEcsSupTmp29 | inc count (9) | Output (non-polled) | 30002/29
| 05-FBk Sensor Temp | localrettemp_1 | ü | AV:1 | data float | 5 | nvoEcsRetTmp29 | inc count (9) | Output (non-polled) | 30290/29
| 06-Over Temp Alarm | unitstat_1 | ü | AV:86 | data float | 6 | nvoEcsStat29 | inc count (9) | Output (non-polled) | 30075/29
| 07-Flow Rate | flowrate_1 | ü | AV:2 | data float | 7 | nvoEcsFlow29 | inc count (9) | Output (non-polled) | 30291/29
E Valve Addr 30
| 01-Cntl Output Signal | boilerstate_2 | ü | AV:12 | data float | 8 | nvoEcsState30 | inc count (9) | Output (non-polled) | 30004/30
| 02-Setpoint | effectsetpt_2 | ü | AV:3 | data float | 9 | nvoEcsSetpt30 | inc count (9) | Output (non-polled) | 30006/30
| 03-RmSetpt | rmsetpt_2 |  | AV:4 | data float | 10 | nviEcsSetptRq30 | inc count (9) | Input (non-polling) | 40027/30
| 04-Outlet Temp | localsuptemp_2 | ü | AV:5 | data float | 11 | nvoEcsSupTmp30 | inc count (9) | Output (non-polled) | 30002/30
| 05-FBk Sensor Temp | localrettemp_2 | ü | AV:6 | data float | 12 | nvoEcsRetTmp30 | inc count (9) | Output (non-polled) | 30290/30
| 06-Over Temp Alarm | unitstat_2 | ü | AV:7 | data float | 13 | nvoEcsStat30 | inc count (9) | Output (non-polled) | 30075/30
| 07-Flow Rate | flowrate_2 | ü | AV:8 | data float | 14 | nvoEcsFlow30 | inc count (9) | Output (non-polled) | 30291/30
E Valve Addr 31
| 01-Cntl Output Signal | boilerstate_3 | ü | AV:9 | data float | 15 | nvoEcsState31 | inc count (9) | Output (non-polled) | 30004/31
| 02-Setpoint | effectsetpt_3 | ü | AV:150 | data float | 16 | nvoEcsSetpt31 | inc count (9) | Output (non-polled) | 30006/31
| 03-RmSetpt | rmsetpt_3 |  | AV:151 | data float | 17 | nviEcsSetptRq31 | inc count (9) | Input (non-polling) | 40027/31
| 04-Outlet Temp | localsuptemp_3 | ü | AV:152 | data float | 18 | nvoEcsSupTmp31 | inc count (9) | Output (non-polled) | 30002/31
| 05-FBk Sensor Temp | localrettemp_3 | ü | AV:153 | data float | 19 | nvoEcsRetTmp31 | inc count (9) | Output (non-polled) | 30290/31
| 06-Over Temp Alarm | unitstat_3 | ü | AV:154 | data float | 20 | nvoEcsStat31 | inc count (9) | Output (non-polled) | 30075/31
| 07-Flow Rate | flowrate_3 | ü | AV:155 | data float | 21 | nvoEcsFlow31 | inc count (9) | Output (non-polled) | 30291/31
E Valve Addr 32
| 01-Cntl Output Signal | boilerstate_4 | ü | AV:10 | data float | 22 | nvoEcsState32 | inc count (9) | Output (non-polled) | 30004/32
| 02-Setpoint | effectsetpt_4 | ü | AV:158 | data float | 23 | nvoEcsSetpt32 | inc count (9) | Output (non-polled) | 30006/32
| 03-RmSetpt | rmsetpt_4 |  | AV:159 | data float | 24 | nviEcsSetptRq32 | inc count (9) | Input (non-polling) | 40027/32
| 04-Outlet Temp | localsuptemp_4 | ü | AV:160 | data float | 25 | nvoEcsSupTmp32 | inc count (9) | Output (non-polled) | 30002/32
| 05-FBk Sensor Temp | localrettemp_4 | ü | AV:161 | data float | 26 | nvoEcsRetTmp32 | inc count (9) | Output (non-polled) | 30290/32
| 06-Over Temp Alarm | unitstat_4 | ü | AV:156 | data float | 27 | nvoEcsStat32 | inc count (9) | Output (non-polled) | 30075/32
| 07-Flow Rate | flowrate_4 | ü | AV:157 | data float | 28 | nvoEcsFlow32 | inc count (9) | Output (non-polled) | 30291/32

## 12CMore-6MLX-4EC,SP-2ACS
BACnet/IP, BACnet MS/TP, Metasys N2, and LonWorks Points List
12 C-Mores, 6 ECS/SP, 4 Modulex and 2 BMS II
Equipment | Point Name | Name |  | Read Only | BACnet Type:ID | N2 Type | N2 ID | Lon SNVT NAME | Lon SNVT | Lon Direction | ModBus/Unit Address
Blr Addr 1
| 01-Fire Rate Out | boilerstate_1 | ü |  | AV:1 | data float | 1 | nvoBlrState1 | inc count (9) | Output (non-polled) | 30009/1
| 02-Active Setpoint | effectsetpt_1 | ü |  | AV:2 | data float | 2 | nvoEffSetpt1 | inc count (9) | Output (non-polled) | 30017/1
| 03-Net Remote Setpt | setpt_1 |  |  | AV:3 | data float | 3 | nviSetpt1 | inc count (9) | Input (non-polling) | 40001/1
| 05-Fire Rate In | boilerload_1 | ü |  | AV:5 | data float | 5 | nvoBlrLoad1 | inc count (9) | Output (non-polled) | 30018/1
| 06-Outlet Temp | localsuptemp_1 | ü |  | AV:6 | data float | 6 | nvoLocSupTmp1 | inc count (9) | Output (non-polled) | 30003/1
| 07-Display Code | dispcode_1 | ü |  | AV:7 | data float | 7 | nvoDispCode1 | inc count (9) | Output (non-polled) | 30001/1
| 08-Unit Status | unitstat_1 | ü |  | AV:8 | data float | 8 | nvoUnitStat1 | inc count (9) | Output (non-polled) | 30002/1
| 09-Run Cycles | runcycles_1 | ü |  | AV:9 | data float | 9 | nvoRunCycles1 | 51 | Output (non-polled) | 30012-30013/1
| 10-Run Hours | runhours_1 | ü |  | AV:10 | data float | 10 | nvoRunHours1 | 51 | Output (non-polled) | 30014-30015/1
Blr Addr 2
| 01-Fire Rate Out | boilerstate_2 | ü |  | AV:11 | data float | 11 | nvoBlrState2 | inc count (9) | Output (non-polled) | 30009/2
| 02-Active Setpoint | effectsetpt_2 | ü |  | AV:12 | data float | 12 | nvoEffSetpt2 | inc count (9) | Output (non-polled) | 30017/2
| 03-Net Remote Setpt | setpt_2 |  |  | AV:13 | data float | 13 | nviSetpt2 | inc count (9) | Input (non-polling) | 40001/2
| 05-Fire Rate In | boilerload_2 | ü |  | AV:15 | data float | 15 | nvoBlrLoad2 | inc count (9) | Output (non-polled) | 30018/2
| 06-Outlet Temp | localsuptemp_2 | ü |  | AV:16 | data float | 16 | nvoLocSupTmp2 | inc count (9) | Output (non-polled) | 30003/2
| 07-Display Code | dispcode_2 | ü |  | AV:17 | data float | 17 | nvoDispCode2 | inc count (9) | Output (non-polled) | 30001/2
| 08-Unit Status | unitstat_2 | ü |  | AV:18 | data float | 18 | nvoUnitStat2 | inc count (9) | Output (non-polled) | 30002/2
| 09-Run Cycles | runcycles_2 | ü |  | AV:19 | data float | 19 | nvoRunCycles2 | 51 | Output (non-polled) | 30012-30013/2
| 10-Run Hours | runhours_2 | ü |  | AV:20 | data float | 20 | nvoRunHours2 | 51 | Output (non-polled) | 30014-30015/2
Blr Addr 3
| 01-Fire Rate Out | boilerstate_3 | ü |  | AV:21 | data float | 21 | nvoBlrState3 | inc count (9) | Output (non-polled) | 30009/3
| 02-Active Setpoint | effectsetpt_3 | ü |  | AV:22 | data float | 22 | nvoEffSetpt3 | inc count (9) | Output (non-polled) | 30017/3
| 03-Net Remote Setpt | setpt_3 |  |  | AV:23 | data float | 23 | nviSetpt3 | inc count (9) | Input (non-polling) | 40001/3
| 05-Fire Rate In | boilerload_3 | ü |  | AV:25 | data float | 25 | nvoBlrLoad3 | inc count (9) | Output (non-polled) | 30018/3
| 06-Outlet Temp | localsuptemp_3 | ü |  | AV:26 | data float | 26 | nvoLocSupTmp3 | inc count (9) | Output (non-polled) | 30003/3
| 07-Display Code | dispcode_3 | ü |  | AV:27 | data float | 27 | nvoDispCode3 | inc count (9) | Output (non-polled) | 30001/3
| 08-Unit Status | unitstat_3 | ü |  | AV:28 | data float | 28 | nvoUnitStat3 | inc count (9) | Output (non-polled) | 30002/3
| 09-Run Cycles | runcycles_3 | ü |  | AV:29 | data float | 29 | nvoRunCycles3 | 51 | Output (non-polled) | 30012-30013/3
| 10-Run Hours | runhours_3 | ü |  | AV:30 | data float | 30 | nvoRunHours3 | 51 | Output (non-polled) | 30014-30015/3
Blr Addr 4
| 01-Fire Rate Out | boilerstate_4 | ü |  | AV:31 | data float | 31 | nvoBlrState4 | inc count (9) | Output (non-polled) | 30009/4
| 02-Active Setpoint | effectsetpt_4 | ü |  | AV:32 | data float | 32 | nvoEffSetpt4 | inc count (9) | Output (non-polled) | 30017/4
| 03-Net Remote Setpt | setpt_4 |  |  | AV:33 | data float | 33 | nviSetpt4 | inc count (9) | Input (non-polling) | 40001/4
| 05-Fire Rate In | boilerload_4 | ü |  | AV:35 | data float | 35 | nvoBlrLoad4 | inc count (9) | Output (non-polled) | 30018/4
| 06-Outlet Temp | localsuptemp_4 | ü |  | AV:36 | data float | 36 | nvoLocSupTmp4 | inc count (9) | Output (non-polled) | 30003/4
| 07-Display Code | dispcode_4 | ü |  | AV:37 | data float | 37 | nvoDispCode4 | inc count (9) | Output (non-polled) | 30001/4
| 08-Unit Status | unitstat_4 | ü |  | AV:38 | data float | 38 | nvoUnitStat4 | inc count (9) | Output (non-polled) | 30002/4
| 09-Run Cycles | runcycles_4 | ü |  | AV:39 | data float | 39 | nvoRunCycles4 | 51 | Output (non-polled) | 30012-30013/4
| 10-Run Hours | runhours_4 | ü |  | AV:40 | data float | 40 | nvoRunHours4 | 51 | Output (non-polled) | 30014-30015/4
Blr Addr 5
| 01-Fire Rate Out | boilerstate_5 | ü |  | AV:41 | data float | 41 | nvoBlrState5 | inc count (9) | Output (non-polled) | 30009/5
| 02-Active Setpoint | effectsetpt_5 | ü |  | AV:42 | data float | 42 | nvoEffSetpt5 | inc count (9) | Output (non-polled) | 30017/5
| 03-Net Remote Setpt | setpt_5 |  |  | AV:43 | data float | 43 | nviSetpt5 | inc count (9) | Input (non-polling) | 40001/5
| 05-Fire Rate In | boilerload_5 | ü |  | AV:45 | data float | 45 | nvoBlrLoad5 | inc count (9) | Output (non-polled) | 30018/5
| 06-Outlet Temp | localsuptemp_5 | ü |  | AV:46 | data float | 46 | nvoLocSupTmp5 | inc count (9) | Output (non-polled) | 30003/5
| 07-Display Code | dispcode_5 | ü |  | AV:47 | data float | 47 | nvoDispCode5 | inc count (9) | Output (non-polled) | 30001/5
| 08-Unit Status | unitstat_5 | ü |  | AV:48 | data float | 48 | nvoUnitStat5 | inc count (9) | Output (non-polled) | 30002/5
| 09-Run Cycles | runcycles_5 | ü |  | AV:49 | data float | 49 | nvoRunCycles5 | 51 | Output (non-polled) | 30012-30013/5
| 10-Run Hours | runhours_5 | ü |  | AV:50 | data float | 50 | nvoRunHours5 | 51 | Output (non-polled) | 30014-30015/5
Blr Addr 6
| 01-Fire Rate Out | boilerstate_6 | ü |  | AV:51 | data float | 51 | nvoBlrState6 | inc count (9) | Output (non-polled) | 30009/6
| 02-Active Setpoint | effectsetpt_6 | ü |  | AV:52 | data float | 52 | nvoEffSetpt6 | inc count (9) | Output (non-polled) | 30017/6
| 03-Net Remote Setpt | setpt_6 |  |  | AV:53 | data float | 53 | nviSetpt6 | inc count (9) | Input (non-polling) | 40001/6
| 05-Fire Rate In | boilerload_6 | ü |  | AV:55 | data float | 55 | nvoBlrLoad6 | inc count (9) | Output (non-polled) | 30018/6
| 06-Outlet Temp | localsuptemp_6 | ü |  | AV:56 | data float | 56 | nvoLocSupTmp6 | inc count (9) | Output (non-polled) | 30003/6
| 07-Display Code | dispcode_6 | ü |  | AV:57 | data float | 57 | nvoDispCode6 | inc count (9) | Output (non-polled) | 30001/6
| 08-Unit Status | unitstat_6 | ü |  | AV:58 | data float | 58 | nvoUnitStat6 | inc count (9) | Output (non-polled) | 30002/6
| 09-Run Cycles | runcycles_6 | ü |  | AV:59 | data float | 59 | nvoRunCycles6 | 51 | Output (non-polled) | 30012-30013/6
| 10-Run Hours | runhours_6 | ü |  | AV:60 | data float | 60 | nvoRunHours6 | 51 | Output (non-polled) | 30014-30015/6
Blr Addr 7
| 01-Fire Rate Out | boilerstate_7 | ü |  | AV:61 | data float | 61 | nvoBlrState7 | inc count (9) | Output (non-polled) | 30009/7
| 02-Active Setpoint | effectsetpt_7 | ü |  | AV:62 | data float | 62 | nvoEffSetpt7 | inc count (9) | Output (non-polled) | 30017/7
| 03-Net Remote Setpt | setpt_7 |  |  | AV:63 | data float | 63 | nviSetpt7 | inc count (9) | Input (non-polling) | 40001/7
| 05-Fire Rate In | boilerload_7 | ü |  | AV:65 | data float | 65 | nvoBlrLoad7 | inc count (9) | Output (non-polled) | 30018/7
| 06-Outlet Temp | localsuptemp_7 | ü |  | AV:66 | data float | 66 | nvoLocSupTmp7 | inc count (9) | Output (non-polled) | 30003/7
| 07-Display Code | dispcode_7 | ü |  | AV:67 | data float | 67 | nvoDispCode7 | inc count (9) | Output (non-polled) | 30001/7
| 08-Unit Status | unitstat_7 | ü |  | AV:68 | data float | 68 | nvoUnitStat7 | inc count (9) | Output (non-polled) | 30002/7
| 09-Run Cycles | runcycles_7 | ü |  | AV:69 | data float | 69 | nvoRunCycles7 | 51 | Output (non-polled) | 30012-30013/7
| 10-Run Hours | runhours_7 | ü |  | AV:70 | data float | 70 | nvoRunHours7 | 51 | Output (non-polled) | 30014-30015/7
Blr Addr 8
| 01-Fire Rate Out | boilerstate_8 | ü |  | AV:71 | data float | 71 | nvoBlrState8 | inc count (9) | Output (non-polled) | 30009/8
| 02-Active Setpoint | effectsetpt_8 | ü |  | AV:72 | data float | 72 | nvoEffSetpt8 | inc count (9) | Output (non-polled) | 30017/8
| 03-Net Remote Setpt | setpt_8 |  |  | AV:73 | data float | 73 | nviSetpt8 | inc count (9) | Input (non-polling) | 40001/8
| 05-Fire Rate In | boilerload_8 | ü |  | AV:75 | data float | 75 | nvoBlrLoad8 | inc count (9) | Output (non-polled) | 30018/8
| 06-Outlet Temp | localsuptemp_8 | ü |  | AV:76 | data float | 76 | nvoLocSupTmp8 | inc count (9) | Output (non-polled) | 30003/8
| 07-Display Code | dispcode_8 | ü |  | AV:77 | data float | 77 | nvoDispCode8 | inc count (9) | Output (non-polled) | 30001/8
| 08-Unit Status | unitstat_8 | ü |  | AV:78 | data float | 78 | nvoUnitStat8 | inc count (9) | Output (non-polled) | 30002/8
| 09-Run Cycles | runcycles_8 | ü |  | AV:79 | data float | 79 | nvoRunCycles8 | 51 | Output (non-polled) | 30012-30013/8
| 10-Run Hours | runhours_8 | ü |  | AV:80 | data float | 80 | nvoRunHours8 | 51 | Output (non-polled) | 30014-30015/8
Blr Addr 9
| 01-Fire Rate Out | boilerstate_9 | ü |  | AV:81 | data float | 81 | nvoBlrState9 | inc count (9) | Output (non-polled) | 30009/9
| 02-Active Setpoint | effectsetpt_9 | ü |  | AV:82 | data float | 82 | nvoEffSetpt9 | inc count (9) | Output (non-polled) | 30017/9
| 03-Net Remote Setpt | setpt_9 |  |  | AV:83 | data float | 83 | nviSetpt9 | inc count (9) | Input (non-polling) | 40001/9
| 05-Fire Rate In | boilerload_9 | ü |  | AV:85 | data float | 85 | nvoBlrLoad9 | inc count (9) | Output (non-polled) | 30018/9
| 06-Outlet Temp | localsuptemp_9 | ü |  | AV:86 | data float | 86 | nvoLocSupTmp9 | inc count (9) | Output (non-polled) | 30003/9
| 07-Display Code | dispcode_9 | ü |  | AV:87 | data float | 87 | nvoDispCode9 | inc count (9) | Output (non-polled) | 30001/9
| 08-Unit Status | unitstat_9 | ü |  | AV:88 | data float | 88 | nvoUnitStat9 | inc count (9) | Output (non-polled) | 30002/9
| 09-Run Cycles | runcycles_9 | ü |  | AV:89 | data float | 89 | nvoRunCycles9 | 51 | Output (non-polled) | 30012-30013/9
| 10-Run Hours | runhours_9 | ü |  | AV:90 | data float | 90 | nvoRunHours9 | 51 | Output (non-polled) | 30014-30015/9
Blr Addr 10
| 01-Fire Rate Out | boilerstate_10 | ü |  | AV:91 | data float | 91 | nvoBlrState10 | inc count (9) | Output (non-polled) | 30009/10
| 02-Active Setpoint | effectsetpt_10 | ü |  | AV:92 | data float | 92 | nvoEffSetpt10 | inc count (9) | Output (non-polled) | 30017/10
| 03-Net Remote Setpt | setpt_10 |  |  | AV:93 | data float | 93 | nviSetpt10 | inc count (9) | Input (non-polling) | 40001/10
| 05-Fire Rate In | boilerload_10 | ü |  | AV:95 | data float | 95 | nvoBlrLoad10 | inc count (9) | Output (non-polled) | 30018/10
| 06-Outlet Temp | localsuptemp_10 | ü |  | AV:96 | data float | 96 | nvoLocSupTmp10 | inc count (9) | Output (non-polled) | 30003/10
| 07-Display Code | dispcode_10 | ü |  | AV:97 | data float | 97 | nvoDispCode10 | inc count (9) | Output (non-polled) | 30001/10
| 08-Unit Status | unitstat_10 | ü |  | AV:98 | data float | 98 | nvoUnitStat10 | inc count (9) | Output (non-polled) | 30002/10
| 09-Run Cycles | runcycles_10 | ü |  | AV:99 | data float | 99 | nvoRunCycles10 | 51 | Output (non-polled) | 30012-30013/10
| 10-Run Hours | runhours_10 | ü |  | AV:100 | data float | 100 | nvoRunHours10 | 51 | Output (non-polled) | 30014-30015/10
Blr Addr 11
| 01-Fire Rate Out | boilerstate_11 | ü |  | AV:101 | data float | 101 | nvoBlrState11 | inc count (9) | Output (non-polled) | 30009/11
| 02-Active Setpoint | effectsetpt_11 | ü |  | AV:102 | data float | 102 | nvoEffSetpt11 | inc count (9) | Output (non-polled) | 30017/11
| 03-Net Remote Setpt | setpt_11 |  |  | AV:103 | data float | 103 | nviSetpt11 | inc count (9) | Input (non-polling) | 40001/11
| 05-Fire Rate In | boilerload_11 | ü |  | AV:105 | data float | 105 | nvoBlrLoad11 | inc count (9) | Output (non-polled) | 30018/11
| 06-Outlet Temp | localsuptemp_11 | ü |  | AV:106 | data float | 106 | nvoLocSupTmp11 | inc count (9) | Output (non-polled) | 30003/11
| 07-Display Code | dispcode_11 | ü |  | AV:107 | data float | 107 | nvoDispCode11 | inc count (9) | Output (non-polled) | 30001/11
| 08-Unit Status | unitstat_11 | ü |  | AV:108 | data float | 108 | nvoUnitStat11 | inc count (9) | Output (non-polled) | 30002/11
| 09-Run Cycles | runcycles_11 | ü |  | AV:109 | data float | 109 | nvoRunCycles11 | 51 | Output (non-polled) | 30012-30013/11
| 10-Run Hours | runhours_11 | ü |  | AV:110 | data float | 110 | nvoRunHours11 | 51 | Output (non-polled) | 30014-30015/11
Blr Addr 12
| 01-Fire Rate Out | boilerstate_12 | ü |  | AV:111 | data float | 111 | nvoBlrState12 | inc count (9) | Output (non-polled) | 30009/12
| 02-Active Setpoint | effectsetpt_12 | ü |  | AV:112 | data float | 112 | nvoEffSetpt12 | inc count (9) | Output (non-polled) | 30017/12
| 03-Net Remote Setpt | setpt_12 |  |  | AV:113 | data float | 113 | nviSetpt12 | inc count (9) | Input (non-polling) | 40001/12
| 05-Fire Rate In | boilerload_12 | ü |  | AV:115 | data float | 115 | nvoBlrLoad12 | inc count (9) | Output (non-polled) | 30018/12
| 06-Outlet Temp | localsuptemp_12 | ü |  | AV:116 | data float | 116 | nvoLocSupTmp12 | inc count (9) | Output (non-polled) | 30003/12
| 07-Display Code | dispcode_12 | ü |  | AV:117 | data float | 117 | nvoDispCode12 | inc count (9) | Output (non-polled) | 30001/12
| 08-Unit Status | unitstat_12 | ü |  | AV:118 | data float | 118 | nvoUnitStat12 | inc count (9) | Output (non-polled) | 30002/12
| 09-Run Cycles | runcycles_12 | ü |  | AV:119 | data float | 119 | nvoRunCycles12 | 51 | Output (non-polled) | 30012-30013/12
| 10-Run Hours | runhours_12 | ü |  | AV:120 | data float | 120 | nvoRunHours12 | 51 | Output (non-polled) | 30014-30015/12
Mlx Addr 13
| 01-Act Mod Lev | boilerstate_13 | ü |  | AV:121 | data float | 121 | nvoMlxState13 | inc count (9) | Output (non-polled) | 41009/13
| 02-Target Setpoint | effectsetpt_13 | ü |  | AV:122 | data float | 122 | nvoMlxSetpt13 | inc count (9) | Output (non-polled) | 41019/13
| 03-Req Outlet Temp | setpt_13 |  |  | AV:123 | data float | 123 | nviMlxSetptRq13 | inc count (9) | Input (non-polling) | 41005/13
| 04-Net Direct Drive | boilercmd_13 |  |  | AV:124 | data float | 124 | nviMlxCmd13 | inc count (9) | Input (non-polling) | 40002/13
| 05-Mod Lev In | boilerload_13 | ü |  | AV:125 | data float | 125 | nvoMlxLoad13 | inc count (9) | Output (non-polled) | 41201/13
| 06-Flow Sens Temp | localsuptemp_13 | ü |  | AV:126 | data float | 126 | nvoMlxSupTmp13 | inc count (9) | Output (non-polled) | 41003/13
| 07-Display Code | dispcode_13 | ü |  | AV:127 | data float | 127 | nvoMlxDispCode13 | inc count (9) | Output (non-polled) | 30001/13
| 11-Error Code | errcode_13 | ü |  | AV:128 | data float | 128 | nvoMlxErrCode13 | 51 | Output (non-polled) | 40001/13
| 08-Unit Status | unitstat_13 | ü |  | AV:129 | data float | 129 | nvoMlxStat13 | inc count (9) | Output (non-polled) | 30002/13
| 09-Ret Flow Temp | returntemp_13 | ü |  | AV:130 | data float | 130 | nvoMlxRetTmp13 | inc count (9) | Output (non-polled) | 41004/13
Mlx Addr 14
| 01-Act Mod Lev | boilerstate_14 | ü |  | AV:131 | data float | 131 | nvoMlxState14 | inc count (9) | Output (non-polled) | 41009/14
| 02-Target Setpoint | effectsetpt_14 | ü |  | AV:132 | data float | 132 | nvoMlxSetpt14 | inc count (9) | Output (non-polled) | 41019/14
| 03-Req Outlet Temp | setpt_14 |  |  | AV:133 | data float | 133 | nviMlxSetptRq14 | inc count (9) | Input (non-polling) | 41005/14
| 04-Net Direct Drive | boilercmd_14 |  |  | AV:134 | data float | 134 | nviMlxCmd14 | inc count (9) | Input (non-polling) | 40002/14
| 05-Mod Lev In | boilerload_14 | ü |  | AV:135 | data float | 135 | nvoMlxLoad14 | inc count (9) | Output (non-polled) | 41201/14
| 06-Flow Sens Temp | localsuptemp_14 | ü |  | AV:136 | data float | 136 | nvoMlxSupTmp14 | inc count (9) | Output (non-polled) | 41003/14
| 07-Display Code | dispcode_14 | ü |  | AV:137 | data float | 137 | nvoMlxDispCode14 | inc count (9) | Output (non-polled) | 30001/14
| 11-Error Code | errcode_14 | ü |  | AV:138 | data float | 138 | nvoMlxErrCode14 | 51 | Output (non-polled) | 40001/14
| 08-Unit Status | unitstat_14 | ü |  | AV:139 | data float | 139 | nvoMlxStat14 | inc count (9) | Output (non-polled) | 30002/14
| 09-Ret Flow Temp | returntemp_14 | ü |  | AV:140 | data float | 140 | nvoMlxRetTmp14 | inc count (9) | Output (non-polled) | 41004/14
Mlx Addr 15
| 01-Act Mod Lev | boilerstate_15 | ü |  | AV:141 | data float | 141 | nvoMlxState15 | inc count (9) | Output (non-polled) | 41009/15
| 02-Target Setpoint | effectsetpt_15 | ü |  | AV:142 | data float | 142 | nvoMlxSetpt15 | inc count (9) | Output (non-polled) | 41019/15
| 03-Req Outlet Temp | setpt_15 |  |  | AV:143 | data float | 143 | nviMlxSetptRq15 | inc count (9) | Input (non-polling) | 41005/15
| 04-Net Direct Drive | boilercmd_15 |  |  | AV:144 | data float | 144 | nviMlxCmd15 | inc count (9) | Input (non-polling) | 40002/15
| 05-Mod Lev In | boilerload_15 | ü |  | AV:145 | data float | 145 | nvoMlxLoad15 | inc count (9) | Output (non-polled) | 41201/15
| 06-Flow Sens Temp | localsuptemp_15 | ü |  | AV:146 | data float | 146 | nvoMlxSupTmp15 | inc count (9) | Output (non-polled) | 41003/15
| 07-Display Code | dispcode_15 | ü |  | AV:147 | data float | 147 | nvoMlxDispCode15 | inc count (9) | Output (non-polled) | 30001/15
| 11-Error Code | errcode_15 | ü |  | AV:148 | data float | 148 | nvoMlxErrCode15 | 51 | Output (non-polled) | 40001/15
| 08-Unit Status | unitstat_15 | ü |  | AV:149 | data float | 149 | nvoMlxStat15 | inc count (9) | Output (non-polled) | 30002/15
| 09-Ret Flow Temp | returntemp_15 | ü |  | AV:150 | data float | 150 | nvoMlxRetTmp15 | inc count (9) | Output (non-polled) | 41004/15
Mlx Addr 16
| 01-Act Mod Lev | boilerstate_16 | ü |  | AV:151 | data float | 151 | nvoMlxState16 | inc count (9) | Output (non-polled) | 41009/16
| 02-Target Setpoint | effectsetpt_16 | ü |  | AV:152 | data float | 152 | nvoMlxSetpt16 | inc count (9) | Output (non-polled) | 41019/16
| 03-Req Outlet Temp | setpt_16 |  |  | AV:153 | data float | 153 | nviMlxSetptRq16 | inc count (9) | Input (non-polling) | 41005/16
| 04-Net Direct Drive | boilercmd_16 |  |  | AV:154 | data float | 154 | nviMlxCmd16 | inc count (9) | Input (non-polling) | 40002/16
| 05-Mod Lev In | boilerload_16 | ü |  | AV:155 | data float | 155 | nvoMlxLoad16 | inc count (9) | Output (non-polled) | 41201/16
| 06-Flow Sens Temp | localsuptemp_16 | ü |  | AV:156 | data float | 156 | nvoMlxSupTmp16 | inc count (9) | Output (non-polled) | 41003/16
| 07-Display Code | dispcode_16 | ü |  | AV:157 | data float | 157 | nvoMlxDispCode16 | inc count (9) | Output (non-polled) | 30001/16
| 11-Error Code | errcode_16 | ü |  | AV:158 | data float | 158 | nvoMlxErrCode16 | 51 | Output (non-polled) | 40001/16
| 08-Unit Status | unitstat_16 | ü |  | AV:159 | data float | 159 | nvoMlxStat16 | inc count (9) | Output (non-polled) | 30002/16
| 09-Ret Flow Temp | returntemp_16 | ü |  | AV:160 | data float | 160 | nvoMlxRetTmp16 | inc count (9) | Output (non-polled) | 41004/16
E Valve Addr 17
| 01-Cntl Output Signal | boilerstate_17 | ü |  | AV:171 | data float | 171 | nvoEcsState17 | inc count (9) | Output (non-polled) | 30004/17
| 02-Setpoint | effectsetpt_17 | ü |  | AV:172 | data float | 172 | nvoEcsSetpt17 | inc count (9) | Output (non-polled) | 30006/17
| 03-RmSetpt | rmsetpt_17 |  |  | AV:173 | data float | 173 | nviEcsSetptRq17 | inc count (9) | Input (non-polling) | 40027/17
| 04-Outlet Temp | localsuptemp_17 | ü |  | AV:174 | data float | 174 | nvoEcsSupTmp17 | inc count (9) | Output (non-polled) | 30002/17
| 05-FBk Sensor Temp | localrettemp_17 | ü |  | AV:175 | data float | 175 | nvoEcsRetTmp17 | inc count (9) | Output (non-polled) | 30170/17
| 06-Over Temp Alarm | unitstat_17 | ü |  | AV:176 | data float | 176 | nvoEcsStat17 | inc count (9) | Output (non-polled) | 30075/17
| 07-Flow Rate | flowrate_17 | ü |  | AV:177 | data float | 177 | nvoEcsFlow17 | inc count (9) | Output (non-polled) | 30171/17
E Valve Addr 18
| 01-Cntl Output Signal | boilerstate_18 | ü |  | AV:181 | data float | 181 | nvoEcsState18 | inc count (9) | Output (non-polled) | 18004/18
| 02-Setpoint | effectsetpt_18 | ü |  | AV:182 | data float | 182 | nvoEcsSetpt18 | inc count (9) | Output (non-polled) | 18006/18
| 03-RmSetpt | rmsetpt_18 |  |  | AV:183 | data float | 183 | nviEcsSetptRq18 | inc count (9) | Input (non-polling) | 40027/18
| 04-Outlet Temp | localsuptemp_18 | ü |  | AV:184 | data float | 184 | nvoEcsSupTmp18 | inc count (9) | Output (non-polled) | 18002/18
| 05-FBk Sensor Temp | localrettemp_18 | ü |  | AV:185 | data float | 185 | nvoEcsRetTmp18 | inc count (9) | Output (non-polled) | 18290/18
| 06-Over Temp Alarm | unitstat_18 | ü |  | AV:186 | data float | 186 | nvoEcsStat18 | inc count (9) | Output (non-polled) | 18075/18
| 07-Flow Rate | flowrate_18 | ü |  | AV:187 | data float | 187 | nvoEcsFlow18 | inc count (9) | Output (non-polled) | 18291/18
E Valve Addr 19
| 01-Cntl Output Signal | boilerstate_19 | ü |  | AV:191 | data float | 191 | nvoEcsState19 | inc count (9) | Output (non-polled) | 30004/19
| 02-Setpoint | effectsetpt_19 | ü |  | AV:192 | data float | 192 | nvoEcsSetpt19 | inc count (9) | Output (non-polled) | 30006/19
| 03-RmSetpt | rmsetpt_19 |  |  | AV:193 | data float | 193 | nviEcsSetptRq19 | inc count (9) | Input (non-polling) | 40027/19
| 04-Outlet Temp | localsuptemp_19 | ü |  | AV:194 | data float | 194 | nvoEcsSupTmp19 | inc count (9) | Output (non-polled) | 30002/19
| 05-FBk Sensor Temp | localrettemp_19 | ü |  | AV:195 | data float | 195 | nvoEcsRetTmp19 | inc count (9) | Output (non-polled) | 30290/19
| 06-Over Temp Alarm | unitstat_19 | ü |  | AV:196 | data float | 196 | nvoEcsStat19 | inc count (9) | Output (non-polled) | 30075/19
| 07-Flow Rate | flowrate_19 | ü |  | AV:197 | data float | 197 | nvoEcsFlow19 | inc count (9) | Output (non-polled) | 30291/19
E Valve Addr 20
| 01-Cntl Output Signal | boilerstate_20 | ü |  | AV:201 | data float | 201 | nvoEcsState20 | inc count (9) | Output (non-polled) | 30004/20
| 02-Setpoint | effectsetpt_20 | ü |  | AV:202 | data float | 202 | nvoEcsSetpt20 | inc count (9) | Output (non-polled) | 30006/20
| 03-RmSetpt | rmsetpt_20 |  |  | AV:203 | data float | 203 | nviEcsSetptRq20 | inc count (9) | Input (non-polling) | 40027/20
| 04-Outlet Temp | localsuptemp_20 | ü |  | AV:204 | data float | 204 | nvoEcsSupTmp20 | inc count (9) | Output (non-polled) | 30002/20
| 05-FBk Sensor Temp | localrettemp_20 | ü |  | AV:205 | data float | 205 | nvoEcsRetTmp20 | inc count (9) | Output (non-polled) | 30290/20
| 06-Over Temp Alarm | unitstat_20 | ü |  | AV:206 | data float | 206 | nvoEcsStat20 | inc count (9) | Output (non-polled) | 30075/20
| 07-Flow Rate | flowrate_20 | ü |  | AV:207 | data float | 207 | nvoEcsFlow20 | inc count (9) | Output (non-polled) | 30291/20
E Valve Addr 21
| 01-Cntl Output Signal | boilerstate_21 | ü |  | AV:211 | data float | 211 | nvoEcsState21 | inc count (9) | Output (non-polled) | 30004/21
| 02-Setpoint | effectsetpt_21 | ü |  | AV:212 | data float | 212 | nvoEcsSetpt21 | inc count (9) | Output (non-polled) | 30006/21
| 03-RmSetpt | rmsetpt_21 |  |  | AV:213 | data float | 213 | nviEcsSetptRq21 | inc count (9) | Input (non-polling) | 40027/21
| 04-Outlet Temp | localsuptemp_21 | ü |  | AV:214 | data float | 214 | nvoEcsSupTmp21 | inc count (9) | Output (non-polled) | 30002/21
| 05-FBk Sensor Temp | localrettemp_21 | ü |  | AV:215 | data float | 215 | nvoEcsRetTmp21 | inc count (9) | Output (non-polled) | 30290/21
| 06-Over Temp Alarm | unitstat_21 | ü |  | AV:216 | data float | 216 | nvoEcsStat21 | inc count (9) | Output (non-polled) | 30075/21
| 07-Flow Rate | flowrate_21 | ü |  | AV:217 | data float | 217 | nvoEcsFlow21 | inc count (9) | Output (non-polled) | 30291/21
E Valve Addr 22
| 01-Cntl Output Signal | boilerstate_22 | ü |  | AV:221 | data float | 221 | nvoEcsState22 | inc count (9) | Output (non-polled) | 30004/22
| 02-Setpoint | effectsetpt_22 | ü |  | AV:222 | data float | 222 | nvoEcsSetpt22 | inc count (9) | Output (non-polled) | 30006/22
| 03-RmSetpt | rmsetpt_22 |  |  | AV:223 | data float | 223 | nviEcsSetptRq22 | inc count (9) | Input (non-polling) | 40027/22
| 04-Outlet Temp | localsuptemp_22 | ü |  | AV:224 | data float | 224 | nvoEcsSupTmp22 | inc count (9) | Output (non-polled) | 30002/22
| 05-FBk Sensor Temp | localrettemp_22 | ü |  | AV:225 | data float | 225 | nvoEcsRetTmp22 | inc count (9) | Output (non-polled) | 30290/22
| 06-Over Temp Alarm | unitstat_22 | ü |  | AV:226 | data float | 226 | nvoEcsStat22 | inc count (9) | Output (non-polled) | 30075/22
| 07-Flow Rate | flowrate_22 | ü |  | AV:227 | data float | 227 | nvoEcsFlow22 | inc count (9) | Output (non-polled) | 30291/22
BMS Addr 128 – for C-More Controller Interface
| 01-Fire Rate Out | boilerstate_128 |  | ü | AV:260 | data float | 228 | nvoBlrState128 | inc count (9) | Output (non-polled) | 30005/128
| 02-Header Set Temp | effectsetpt_128 |  | ü | AV:261 | data float | 229 | nvoEffSetpt128 | inc count (9) | Output (non-polled) | 30006/128
| 03-Net Header Set Temp | setpt_128 |  |  | AV:262 | data float | 230 | nviSetpt128 | inc count (9) | Input (non-polling) | 40005/128
| 04-Header Temp | localsuptemp_128 |  | ü | AV:263 | data float | 231 | nvoLocSupTmp128 | inc count (9) | Output (non-polled) | 30002/128
| 05-Outside Air Temp | localoatemp_128 |  | ü | AV:264 | data float | 232 | nvoLocOATmp128 | inc count (9) | Output (non-polled) | 30003/128
| 06-Display Code | dispcode_128 |  | ü | AV:265 | data float | 233 | nvoDispCode128 | inc count (9) | Output (non-polled) | 30011/128
| 07-Num Boilers Fired | blrfired_128 |  | ü | AV:266 | data float | 234 | nvoBlrsFired128 | inc count (9) | Output (non-polled) | 30008/128
| 08-Num Boilers Online | blronline_128 |  | ü | AV:267 | data float | 235 | nvoBlrsOnline128 | inc count (9) | Output (non-polled) | 30009/128
| 09-Last Blr Fired | blrlast_128 |  | ü | AV:268 | data float | 236 | nvoLastBlrFired128 | inc count (9) | Output (non-polled) | 30017/128
| 10-Boiler 1 Status | blr1stat_128 |  | ü | AV:269 | data float | 237 | nvoBlr1Stat128 | inc count (9) | Output (non-polled) | 30018/128
| 11-Boiler 2 Status | blr2stat_128 |  | ü | AV:270 | data float | 238 | nvoBlr2Stat128 | inc count (9) | Output (non-polled) | 30019/128
| 12-Boiler 3 Status | blr3stat_128 |  | ü | AV:271 | data float | 239 | nvoBlr3Stat128 | inc count (9) | Output (non-polled) | 30020/128
| 13-Boiler 4 Status | blr4stat_128 |  | ü | AV:272 | data float | 240 | nvoBlr4Stat128 | inc count (9) | Output (non-polled) | 30021/128
| 14-Boiler 5 Status | blr5stat_128 |  | ü | AV:273 | data float | 241 | nvoBlr5Stat128 | inc count (9) | Output (non-polled) | 30022/128
| 15-Boiler 6 Status | blr6stat_128 |  | ü | AV:274 | data float | 242 | nvoBlr6Stat128 | inc count (9) | Output (non-polled) | 30023/128
| 16-Boiler 7 Status | blr7stat_128 |  | ü | AV:275 | data float | 243 | nvoBlr7Stat128 | inc count (9) | Output (non-polled) | 30024/128
| 17-Boiler 8 Status | blr8stat_128 |  | ü | AV:276 | data float | 244 | nvoBlr8Stat128 | inc count (9) | Output (non-polled) | 30025/128
| 18-Net Blr 1 Status | blr9stat_128 |  | ü | AV:277 | data float | 245 | nvoNetBlr1Stat128 | inc count (9) | Output (non-polled) | 30026/128
| 19-Net Blr 2 Status | blr10stat_128 |  | ü | AV:278 | data float | 246 | nvoNetBlr2Stat128 | inc count (9) | Output (non-polled) | 30027/128
| 20-Net Blr 3 Status | blr11stat_128 |  | ü | AV:279 | data float | 247 | nvoNetBlr3Stat128 | inc count (9) | Output (non-polled) | 30028/128
| 21-Net Blr 4 Status | blr12stat_128 |  | ü | AV:280 | data float | 248 | nvoNetBlr4Stat128 | inc count (9) | Output (non-polled) | 30029/128
| 22-Net Blr 5 Status | blr13stat_128 |  | ü | AV:281 | data float | 249 | nvoNetBlr5Stat128 | inc count (9) | Output (non-polled) | 30030/128
| 23-Net Blr 6 Status | blr14stat_128 |  | ü | AV:282 | data float | 250 | nvoNetBlr6Stat128 | inc count (9) | Output (non-polled) | 30031/128
| 24-Net Blr 7 Status | blr15stat_128 |  | ü | AV:283 | data float | 251 | nvoNetBlr7Stat128 | inc count (9) | Output (non-polled) | 30032/128
| 25-Net Blr 8 Status | blr16stat_128 |  | ü | AV:284 | data float | 252 | nvoNetBlr8Stat128 | inc count (9) | Output (non-polled) | 30033/128
| 26-Net Blr 9 Status | blr17stat_128 |  | ü | AV:285 | data float | 253 | nvoNetBlr9Stat128 | inc count (9) | Output (non-polled) | 30034/128
| 27-Net Blr 10 Status | blr18stat_128 |  | ü | AV:286 | data float | 254 | nvoNetBlr10Stat128 | inc count (9) | Output (non-polled) | 30035/128
| 28-Net Blr 11 Status | blr19stat_128 |  | ü | AV:287 | data float | 255 | nvoNetBlr11Stat128 | inc count (9) | Output (non-polled) | 30036/128
| 29-Net Blr 12 Status | blr20stat_128 |  | ü | AV:288 | data float | 256 | nvoNetBlr12Stat128 | inc count (9) | Output (non-polled) | 30037/128
BMS Addr 228 – for Modulex BCM Interface
| 01-Fire Rate Out | boilerstate_228 |  | ü | AV:300 | data float | 161 | nvoBlrState228 | inc count (9) | Output (non-polled) | 30005/228
| 02-Header Set Temp | effectsetpt_228 |  | ü | AV:301 | data float | 162 | nvoEffSetpt228 | inc count (9) | Output (non-polled) | 30006/228
| 03-Net Header Set Temp | setpt_228 |  |  | AV:302 | data float | 163 | nviSetpt228 | inc count (9) | Input (non-polling) | 40005/228
| 04-Header Temp | localsuptemp_228 |  | ü | AV:303 | data float | 164 | nvoLocSupTmp228 | inc count (9) | Output (non-polled) | 30002/228
| 05-Outside Air Temp | localoatemp_228 |  | ü | AV:304 | data float | 165 | nvoLocOATmp228 | inc count (9) | Output (non-polled) | 30003/228
| 06-Display Code | dispcode_228 |  | ü | AV:305 | data float | 166 | nvoDispCode228 | inc count (9) | Output (non-polled) | 30011/228
| 07-Num Boilers Fired | blrfired_228 |  | ü | AV:306 | data float | 167 | nvoBlrsFired228 | inc count (9) | Output (non-polled) | 30008/228
| 08-Num Boilers Online | blronline_228 |  | ü | AV:307 | data float | 168 | nvoBlrsOnline228 | inc count (9) | Output (non-polled) | 30009/228
| 09-Last Blr Fired | blrlast_228 |  | ü | AV:308 | data float | 169 | nvoLastBlrFired228 | inc count (9) | Output (non-polled) | 30017/228
| 18-Net Blr 1 Status | blr9stat_228 |  | ü | AV:309 | data float | 170 | nvoNetBlr1Stat228 | inc count (9) | Output (non-polled) | 30026/228
| 19-Net Blr 2 Status | blr10stat_228 |  | ü | AV:310 | data float | 178 | nvoNetBlr2Stat228 | inc count (9) | Output (non-polled) | 30027/228
| 20-Net Blr 3 Status | blr11stat_228 |  | ü | AV:311 | data float | 179 | nvoNetBlr3Stat228 | inc count (9) | Output (non-polled) | 30028/228
| 21-Net Blr 4 Status | blr12stat_228 |  | ü | AV:312 | data float | 180 | nvoNetBlr4Stat228 | inc count (9) | Output (non-polled) | 30029/228