SECTION 235217: 3-10 MMBTU MFC SERIES CONDENSING BOILERS

- PART 1 - GENERAL

## 1.1	RELATED DOCUMENTS

A.	Drawings and general provisions of the Contract apply to this Section, including General and Supplementary Conditions and Division 01 Specification Sections.

## 1.2	SUMMARY

A.	This Section includes factory-fabricated and field-assembled, dual fuel, natural gas/propane-fired, #2 fuel oil (as backup), fire-tube condensing boilers, trim and accessories for generating hot water.

## 1.3	SUBMITTALS

- A.	Product Data: Include performance data, operating characteristics, furnished specialties and accessories.

- Prior to flue vent installation, engineered calculations and drawings must be submitted to Architect/Engineer to thoroughly demonstrate that size and configuration conform to recommended size, length and footprint for each submitted boiler.

- B.	Pressure Drop Curve. Submit pressure drop curve for the following flow ranges:

- MFC 3000: 0-350 GPM

- MFC 4000: 0-520 GPM

- MFC 5000: 0-610 GPM

- MFC 6000: 0-750 GPM

- MFC 8000: 0-1000 GPM

- MFC 10000: 0-1100 GPM

- If submitted material is different from that of the design basis, boiler manufacture shall incur all costs associated with pump substitution.

- C.	Shop Drawings: For boilers, boiler trim and accessories include:

- Plans, elevations, sections, details and attachments to other work

- Wiring Diagrams for power, signal and control wiring

- D.	Source Quality Control Test Reports: Reports shall be included in submittals.

- E.	Field Quality Control Test Reports: Reports shall be included in submittals.

- F.	Operation and Maintenance Data: Data to be included in boiler emergency, operation and maintenance manuals.

- G.	Warranty: Standard warranty specified in this Section

- H.	Other Informational Submittals:

          - ASME Stamp Certification and Report: Submit “H" stamp certificate of authorization, as required by authorities having jurisdiction, and document hydrostatic testing of piping external to boiler.

            - Submit ASME “U” stamp certificate for the 4th pass.

- 1.4	QUALITY ASSURANCE

- A.	Electrical Components, Devices and Accessories: Boilers must be listed and labeled as defined in NFPA 70, Article 100, by a testing agency acceptable to authorities having jurisdiction, and marked for intended use.

- B.	ASME Compliance: Condensing boilers must be constructed in accordance with ASME Boiler and Pressure Vessel Code, Section IV “Heating Boilers”.  Boiler shall comply with CSD-1 code requirements.

- C.	ASHRAE/IESNA 90.1 Compliance: Boilers shall have minimum efficiency according to "Gas and Oil Fired Boilers - Minimum Efficiency Requirements."

- D.	UL Compliance: Boiler burner must be in compliance with UL 295, "Commercial-Industrial Gas Burners" and UL 296, “Standard For Safety Oil Burners.  Burners shall be listed and labeled by a testing agency acceptable to authorities having jurisdiction.

- Boiler components must be UL listed. If alternate listing is used, manufacturer must provide test data showing that the product was tested and certified to meet equal/similar UL standards.

- E.	Emission Standards. When operating on natural gas and installed and operated in accordance with manufacturer’s instructions, all boilers shall have CO emissions less than 100 ppm and the following NOx emissions corrected to 3% oxygen at all firing rates:

- MFC 3000		<30 ppm

- MFC 4000		<30 ppm

- MFC 5000		<30 ppm

- MFC 6000		<40 ppm

- MFC 8000		<40 ppm

- MFC 10000	<40 ppm

- Optional Low NOx burner shall be sourced to meet local requirements.

- When operating on #2 fuel oil, all boiler models shall have CO emissions less than 100 ppm corrected to 3% oxygen at all firing rates.

- 1.5	COORDINATION

- A.	Coordinate size and location of concrete bases. Cast anchor-bolt inserts into bases. Concrete, reinforcement and formwork requirements are specified in Division 03.

- 1.6	WARRANTY

- A.	Standard Warranty: Boilers shall include manufacturer's standard form in which manufacturer agrees to repair or replace components of boilers that fail in materials or workmanship within specified warranty period.

          - Warranty Period for Fire-Tube Condensing Boilers

- The pressure vessel/heat exchanger shall carry a 5-year from shipment, non-prorated, limited warranty against any failure due to condensate corrosion, thermal stress, mechanical defects or workmanship.

- Manufacturer labeled control panels are conditionally warranted against failure for 18 months from shipment.

- All other components, with the exception of the igniter and flame detector, are conditionally guaranteed against any failure for 18 months from shipment

- PRODUCTS

      - MANUFACTURERS

- A.	Basis-of-Design is the MFC Series Condensing Boilers as supplied by AERCO International Inc. Equivalent units and manufacturers must meet all performance criteria, and will be considered upon prior approval.

      - CONSTRUCTION

- A.	Description: Boiler shall be a multi-fuel natural gas, propane, or #2 oil fired (backup fuel), fully condensing when firing on gaseous fuels, 4-pass fire tube design. Boiler efficiency shall increase with decreasing load (output), while maintaining setpoint. Boiler shall be fabricated fire-tube condensing boiler with heat exchanger sealed pressure-tight, built on a steel base, and shall include insulated jacket, flue-gas vent, combustion-air intake connections, water supply, return and condensate drain connections, and controls.

- B.	Heat Exchanger: The heat exchanger shall be a 4-pass combustion flow firetube design. The first 3-passes shall be of carbon steel construction for high heat transfer and low thermal stresses, and the final 4th pass (area of heat exchanger where the flue gases will condense) shall be of 316Ti or 439 stainless steel construction. The pressure vessel/heat exchanger shall be welded construction.  The heat exchanger shall be ASME stamped for a working pressure of 80 psig and maximum working temperature of 240°F.

- Boilers with heat exchangers using carbon steel only or cast iron design will be deemed unacceptable. Non-condensing boilers will likewise be deemed unacceptable. Boilers with aluminum inserts will be deemed unacceptable due to their risk for fouling and erosion when firing #2 fuel oil.

- Access to the tubesheets and heat exchanger shall be available via a flat front door with reversible opening, inner high-insulating ceramic casing, pivoted on hinges, by burner or exhaust manifold removal.

- C.	The boiler pressure drop shall not exceed the following per model size:

- MFC 3000 – 2.4 psig @ 300 gpm

- MFC 4000 – 1 psig @ 400 gpm

- MFC 5000 – 1.3 psig @ 500 gpm

- MFC 6000 – 1.9 psig @ 600 gpm

- MFC 8000 – 1.1 psig @ 800 gpm

- MFC 10000 – 1.7 psig @ 1000 gpm

- Due to their inherent high waterside pressure drop, watertube designs will be deemed unacceptable.

The boiler shall be able to operate in low-to-near zero flow conditions without any harm to the heat exchanger or pressure vessel. The boiler shall be able to be installed in a primary-variable application.  Boilers that require primary/secondary piping arrangements will be deemed unacceptable.

The boiler shall feature dual return connections for low and high return temperature zones for added flexibility and optimization for thermal efficiency.  Boilers without this feature from other manufacturers will be deemed unacceptable.

Inspection openings in the pressure vessel shall be in accordance with ASME Section IV pressure vessel code.  The boiler shall be designed so that the thermal efficiency increases as the boiler firing rate decreases.

- D.	The burner shall produce NOx emissions referenced in section 1.4 F, when firing on natural gas.

- The burner itself shall be a forced draft power burner type.  The burner mounting flange shall support the entire burner weight without any additional support. The burner shall feature a stainless steel flame retention combustion head capable of withstanding temperatures in excess of 1400° F.  The combustion head shall utilize a diffuser and sleeve to direct excess air directly through the diffuser or around the flame.  The diffuser insertion shall have the capability to be adjusted.  The burner shall allow the flame to be viewed via an inspection window without the removal of any covers.  Additionally, the burner shall utilize a high efficiency TEFC type blower.  A precision servo-motor connected to a butterfly valve shall be used to control airflow.

- E.	Dual Fuel Capability.  The boiler shall include provisions for dual fuel capability (natural gas/propane as main fuel, #2 fuel oil as backup).  The system shall incorporate independent natural gas and/or propane gas trains, oil train and a fuel selector switch.  Gas trains shall be CSD-1 compliant.  This switching mechanism shall be such that it shall not be possible to flow both fuels simultaneously.  The unit shall be calibrated to run on both fuel sources at start-up. No additional re-calibration shall be required when switching between fuel sources for a period of one year from initial calibration. All fuel piping connections must be factory supplied.

- A compressed air supply shall not be required to fire on #2 fuel oil. The factory shall supply the boiler oil pump set along with provisions to mount on the boiler unit. An integral regulator to adjust the flow of oil to the burner nozzles must be included with the oil pump.

- F.	Exhaust Manifold: The exhaust manifold shall be of corrosion resistant 316 stainless steel. Connections are specified in Part 2.6. The exhaust manifold shall have a collecting reservoir and a gravity drain for the elimination of condensation.

- G.	Blower: The boiler shall include a VFD controlled or constant speed fan to operate during the burner firing sequence and pre-purge the combustion chamber.

- Motors: Blower motors shall comply with requirements specified in Division 23 Section "Common Motor Requirements for HVAC Equipment."

- H.	Ignition: Ignition shall be via spark ignition (either direct or proven pilot) with 100 percent main-valve shutoff and electronic flame supervision.

- I.	The boiler shall be designed such that the combustion air may be drawn from the mechanical room itself or ducted combustion air from outside.

      - CONTROLS

        - Refer to Division 23, Section “Instrumentation and Control of HVAC.”

        - The boiler control system shall be Underwriters Laboratories recognized.

        - Flame Safeguard Control: Boiler flame safeguard control shall be Siemens LMV series full linkageless operation with servo motors to control the air and fuel supply for combustion.

        - The combustion safeguard/flame monitoring system shall use proven pilot and a main burner rectification-type flame sensor or UV/optical sensor.

        - The control panel hardware shall support RS-232 or RS-485 remote communications.

        - The controls shall annunciate boiler and sensor status and include extensive self-diagnostic capabilities.

        - The boiler control system shall incorporate the following additional features for enhanced external system interface:

- System start temperature feature

- Pump delay timer

- Auxiliary start delay timer

- Analog output feature to enable simple monitoring of temperature setpoint, outlet temperature or fire rate

- Remote interlock circuit

- Delayed interlock circuit

- Fault relay for remote fault alarm

        - Each boiler shall include an electric, single-seated combination safety shutoff valve/regulator with proof of closure switch in its gas train. Each boiler shall incorporate dual over-temperature protection with manual reset, in accordance with ASME Section IV and CSD-1.

        - For boiler plants with 2 or more units, the Boiler Manufacturer shall supply as part of the boiler package a sequencing control system to control all operation and energy input of the multiple boiler heating plant. The sequencing control system shall be comprised of a microprocessor based control than can modulate up to 4 boilers.

- The sequencing controller shall have the ability to vary the firing rate and energy input of each individual boiler throughout its full modulating range to maximize the condensing capability and thermal efficiency output of the entire heating plant. The controller shall be a PID type controller and uses parallel or sequential modulation for accurate temperature control with excellent variable load response.  The controller shall provide contact closure for auxiliary equipment such as system pumps and combustion air inlet dampers based upon outdoor air temperature.

- The sequencing controller shall have the following anti-cycling features:

- Manual designation of lead boiler and last boiler.

- Lead boiler rotation based on run time equalization.

- Adjustable firing delay, modulation delay, and boiler stage delay.

- When in Setpoint operation mode, the sequencing controller target temperature shall be fully field adjustable up to 225ºF. When set on Outdoor Temperature Reset, the controller uses a characterized heating curve to determine the rate at which the water temperature is changed as a function of outdoor temperature. The characterized heating curve shall be adjustable to suit the type of terminal units used in the system.

- The controller shall be capable of receiving a setpoint via Modbus or external DC signal from a Building Automation System. To provide greater energy savings, the controller shall have programmable daily or weekly schedules, and customizable for occupied and unoccupied periods.

      - ELECTRICAL POWER

        - Controllers, Electrical Devices and Wiring: Electrical devices and connections are specified in product O&M manual and electrical guide.

        - Single-Point Field Power Connection: Factory-installed and factory-wired switches, motor controllers, transformers, and other electrical devices shall provide a single-point field power connection to the boiler. 120V/1PH/60Hz shall be for the control system while the main blower/burner shall utilize the voltage options listed under Electrical Characteristics:

        - Electrical Characteristics:

- Option 1	Option 2			Option 3

- Voltage: 	208 V	460 V				575 V

- Phase: 	Three	Three				Three

- Frequency: 	60 Hz	60 Hz				60 Hz

- Full-Load Current 	16-25 Amps	8-13 Amps			7-11 Amps

      - VENTING

        - The exhaust vent must be UL Listed for use with Category II and IV appliances condensing flue gas service. UL-listed vents Al 29-4C stainless steel must be used with boilers.

        - The minimum exhaust vent duct size for each boiler is 10-inch (MFC 3000), 12-inch (MFC 4000/5000), 14-inch (MFC 6000), and 16-inch diameter (MFC 8000/10000).

        - Combustion-Air Intake: Boilers shall be capable of drawing combustion air from the outdoors via a metal or PVC duct connected between the boiler and the outdoors.

        - The minimum ducted combustion air duct size for each boiler is 10-inch (MFC 3000), 12-inch (MFC 4000/5000), 14-inch (MFC 6000), and 16-inch diameter (MFC 8000/10000).

        - Common vent and common combustion air must be an available option for boiler installation. Consult manufacturer for common vent and combustion air sizing.

        - Follow guidelines specified in manufacturer’s venting guide.

      - SOURCE QUALITY CONTROL

        - Hydrostatic Test: Perform hydrostatic testing.

        - Inspect factory-assembled boilers, before shipping, according to ASME Boiler and Pressure Vessel Code. Optional fire test may be available. This testing includes optional combustion calibration, checking of boiler safeties, and performance, including boiler turndown – Each Boiler must be certified up to 5:1 turndown (gaseous fuels) during the factory testing to assure performance.

          - If boilers are not factory assembled and fire-tested, the local vendor is responsible for all field assembly and testing.

        - Allow Owner access to source quality-control testing of boilers. Notify Architect fourteen days in advance of testing.

- EXECUTION

      - EXAMINATION

- A.	Before boiler installation examine roughing-in for concrete equipment bases, anchor-bolt sizes and locations and piping and electrical connections to verify actual locations, sizes and other conditions affecting boiler performance, maintenance and operations.

          - Final boiler locations indicated on Drawings are approximate. Determine exact locations before roughing-in for piping and electrical connections.

        - Examine mechanical spaces for suitable conditions where boilers will be installed.

        - Proceed with installation only after unsatisfactory conditions have been corrected.

      - BOILER INSTALLATION

        - Install boilers level on concrete bases. Concrete base is specified in Division 23 Section "Common Work Results for HVAC," and concrete materials and installation requirements are specified in Division 03.

        - Install gas-fired boilers according to NFPA 54.

        - Install oil-fired boilers according to NFPA 31.

        - Assemble and install boiler trim.

        - Install electrical devices furnished with boiler but not specified to be factory mounted.

        - Install control wiring to field-mounted electrical devices.

      - CONNECTIONS

        - Piping installation requirements are specified in other Division 23 sections. Drawings indicate general arrangement of piping, fittings and specialties.

        - Install piping adjacent to boiler to permit service and maintenance.

        - Install piping from equipment drain connection to nearest floor drain. Piping shall be at least full size of connection. Provide an isolation valve if required.

        - Install condensate piping from the drain on the exhaust manifold to the factory supplied condensate trap and optional condensate neutralizer and then pipe to a floor drain. The piping should be either PVC or Polypropylene; copper should not be used.

        - Connect gas piping to boiler gas-train inlet with unions. Piping shall be at least full size of gas train connection. Provide a reducer if required.

        - Connect hot-water piping to supply and return boiler tappings with shutoff valve and union or flange at each connection as close as possible.

        - Install piping from safety relief valves to nearest floor drain. Piping must remain at a minimum the same size of the relief valve outlet.

        - Boiler Venting

- Install flue venting kit and combustion-air intake.

        - Ground equipment according to Division 26 Section "Grounding and Bonding for Electrical Systems."

        - Connect wiring according to Division 26 Section "Low-Voltage Electrical Power Conductors and Cables."

      - FIELD QUALITY CONTROL

- A.	Perform tests and inspections and prepare test reports.

          - Manufacturer's Field Service: Engage a factory-authorized service representative to inspect components, assemblies and equipment installations, including connections, and to assist in testing.

- B.	Tests and Inspections

- 1.	Perform installation and startup checks according to manufacturer's written instructions.

- 2.	Perform hydrostatic test. Repair leaks and retest until no leaks exist.

- 3.	Start units to confirm proper motor rotation and unit operation. Adjust air-fuel ratio and combustion.

- 4.	Test and adjust controls and safeties. Replace damaged and malfunctioning controls and equipment.

- a.	Check and adjust initial operating set points and high- and low-limit safety set points of fuel supply, water level and water temperature.

- b.	Set field-adjustable switches and circuit-breaker trip ranges as indicated.

- C.	Remove and replace malfunctioning units and retest as specified above.

- D.	Occupancy Adjustments: When requested within 2 months of date of Substantial Completion, provide on-site assistance adjusting system to suit actual occupied conditions. Provide up to two visits to Project during other than normal occupancy hours for this purpose.

- E.	Performance Tests:

- The boiler manufacturer is expected to provide partial load thermal efficiency curves. These thermal efficiency curves must include at least three separate curves at various BTU input levels (20%, 50%, 100% input). If these curves are not available, it is the responsibility of the boiler manufacturer to complete the following performance tests:

- Engage a factory-authorized service representative to inspect component assemblies and equipment installations, including connections, and to conduct performance testing.

- Boilers shall comply with performance requirements indicated, as determined by field performance tests. Adjust, modify, or replace equipment to comply.

- Repeat tests until results comply with requirements indicated.

- Provide analysis equipment required to determine performance.

- Provide temporary equipment and system modifications necessary to dissipate the heat produced during tests if building systems are not adequate.

- Notify Architect in advance of test dates.

- Document test results in a report and submit to Architect.

END OF SECTION 235216