Furnish and install as shown on AERCO International plans and operation and maintenance manuals, with all applicable codes and authorities having local, state and federal jurisdiction, AM Series Water Heater Model AM _____R. The water heater plant shall consist of ____ water heater(s) as manufactured by AERCO International, Inc. Each water heater shall be CSA Listed, CSD-1 and UL low-lead compliant, and incorporate a gas train designed in accordance with Factory Mutual. Each water heater shall have an input and gross output as shown in the table below (dependent upon return water temperature) when fired at full fire with natural gas. Electrical service to each unit shall be 120V/1/60Hz 15 amp service. The water heater control panel shall be proprietary in design and incorporate the functions of thermal controller, combustion safeguard control, message annunciation, and fault diagnostic display, on individual field replaceable circuit boards mounted within a single housing. Each water heater shall have a footprint of no more than 24” W, 40” D, and 71.3” H. The water heater installed weight shall not exceed the weights shown in the table below when filled. The water heater shall have an ASME approved relief valve setting of 125 psig.  The water heater shall have an integrated 32 gallon thermal buffer tank and integrated constant speed pump.

| Model | Input (MBTU) | Output (BMTU) | Weight, Wet (lbs.) |
| --- | --- | --- | --- |
| AM 199R | 199 | 183-195 | 550 |
| AM 250R | 250 | 230-245 | 630 |
| AM 399R | 399 | 367-391 | 815 |
| AM 500R | 500 | 460-490 | 930 |

Construction

Water heater modules shall be gas fired (natural gas unit or propane unit), condensing, modular, stainless steel water-tube design with a modulating forced draft power burner and positive pressure vent discharge.

Burner, Modulating Gas Valve, and Variable Speed Fan

The water heater, which consists of the number of thermal modules and turndown ratios shown below, shall operate without loss of combustion efficiency.  Each thermal module’s premix burner shall be metal fiber mesh covering a stainless steel head, with spark ignition and flame rectification.  All burner material exposed to the combustion zone shall be of stainless steel construction. There shall be no moving parts within the burner itself. The burners shall produce <20 ppm of NOx corrected to 3% excess oxygen.  A modulating gas valve and variable speed fan shall meter the natural gas and air input, respectively.   Each module will have a check valve with proving switch in between the fan and burner to indicate in the event of blocked or malfunctioning fan.

| Model | Thermal Modules | Turndown Ratio |
| --- | --- | --- |
| AM 199R | 1 | 4:1 |
| AM 250R | 1 | 5:1 |
| AM 399R | 2 | 8:1 |
| AM 500R | 2 | 10:1 |

Heat Exchanger

The heat exchanger is constructed of stainless steel and shall be capable of handling return water temperatures down to 40° F without any failure due to thermal shock or fireside condensation. It shall be ASME stamped for a working pressure not less than 160 psig.  Each module shall be equipped with a water flow meter capable of measuring water flow rates into each heat exchanger.

The water heater shall be designed so that the thermal efficiency increases as the water heater firing rate decreases. The heat exchanger shall be stainless steel construction. Access to the fireside of the thermal modules is available by burner assembly removal. Minimum access opening shall be no less than 6 ¼” diameter circle per thermal module.

Exhaust Manifold, Condensate Trap, and Condensate Neutralizer

The exhaust manifold shall be of polypropylene with a 3” diameter flue connection for 199/250R or 4”diameter flue connection for 399/500R. The exhaust manifold shall terminate in a condensate trap.  The condensate trap shall have a gravity drain for the elimination of the condensation into an integrated condensate neutralizer.

WATER HEATER Controls

The water heater control system shall consist of a master controller (Argus Controller) to which individual thermal module controllers are linked as slaves. The entire system shall be CSA or UL Recognized. Each of the thermal module controllers shall consist of a combustion safeguard and flame monitoring system. Individual thermal module controllers shall be field replaceable. The combustion safeguard/flame monitoring system shall utilize spark ignition and a rectification type flame sensor. The water heater control system shall annunciate water heater & sensor status and include extensive self-diagnostic capabilities.

An optional second communications board shall allow third party Building Automation System (BAS) to control and monitor the water heater via Modbus RS-485 communications.

Each water heater shall incorporate dual over-temperature protection with manual reset and either a flow switch or low water cut out, both in accordance with ASME Section IV and CSD-1.

Temperature Control Modes

The AM series water heater(s) shall operate in the control modes listed below:

__ 1. Internal Setpoint

__ 2. Indoor/Outdoor Reset

__ 3. 0 to 10VDC Temperature Setpoint

__ 4. Network Temperature Setpoint

The following is a description of each control mode.

Internal Setpoint: Water heater shall include integral factory wired operating controls to control all operation and energy input of the water heater. Control of discharge water temperature shall be set through an internal setpoint with an adjustment of 68ºF to 189ºF. The individual thermal module controllers shall vary their respective thermal module’s input throughout its full range to maximize the condensing capability of the water heater.

The water heater will operate to maintain a constant buffer tank temperature. Unit shall operate with an Inverse Efficiency Curve, with known Part Load Value Efficiencies. Maximum efficiency shall be achieved at minimum firing input. Controls shall be fully field adjustable from 68ºF to 189ºF in operation.  The water heater shall have LCD display for monitoring of all sensors and interlocks.

Indoor/Outdoor Reset: Water heater shall include integral factory wired operating controls to control all operation and energy input of the water heater plant. The individual thermal module controllers shall vary their respective thermal module’s input throughout its full range to maximize the condensing capability of the water heater. The water heater will operate to vary buffer tank temperature setpoint on an inverse ratio in response to outdoor temperature to control buffer tank temperature.

Unit shall operate with an Inverse Efficiency Curve, with known Part Load Value Efficiencies. Maximum efficiency shall be achieved at minimum firing input. The water heater shall have LCD display for monitoring of all sensors and interlocks.

0VDC to 10VDC Temperature Setpoint: Water heater shall include integral factory wired operating controls to control all operation and energy input of the water heater. The individual thermal module controllers shall vary their respective thermal module’s input throughout its full range to maximize the condensing capability of the water heater.

The water heater will operate to vary buffer tank temperature setpoint linearly as an externally applied 0 VDC to 10 VDC signal is supplied to the E8 Controller. Unit shall operate with an Inverse Efficiency Curve, with known Part Load Value Efficiencies. Maximum efficiency shall be achieved at minimum firing input. The water heater shall have LCD display for monitoring of all sensors and interlocks.

Network Temperature Setpoint: Water heater shall include integral factory wired operating controls to control all operation and energy input of the water heater. The individual thermal module controllers shall vary their respective thermal module’s input throughout its full range to maximize the condensing capability of the water heater.

The water heater will operate to vary buffer tank temperature setpoint as an external communication utilizing the MODBUS protocol is supplied to the water heater’s communications module via the RS-485 port. Unit shall operate with an Inverse Efficiency Curve, with known Part Load Value Efficiencies. Maximum efficiency shall be achieved at minimum firing input. The water heater shall have LCD display for monitoring of all sensors and interlocks.

Controls Interoperability

The communications module shall utilize the MODBUS open protocol to interface with third party Building Automation Systems (BAS).

Controls interface with BACnet, Lonworks, and N2 shall utilize an optional AERCO Communications Gateway to act as a MODBUS interface/translator between the BAS the communications.  The AERCO Communications Gateway shall be comprised of a microprocessor based control utilizing the MODBUS protocol to communicate with the water heaters.  Non-volatile backup of all point mappings and programs shall be internally provided as standard.  Connection between Gateway and individual water heaters shall be “daisy chain” with shielded, twisted-pair, low voltage wiring for ease of installation.

INSTALLATION

All aspects of installation of Water Heater Plant shall be in strict accordance with manufacturer's instructions. The vent system must conform to all manufacturer’s recommendations and shall utilize UL listed stainless steel AL-29-4C, Polypropylene, PVC, or CPVC Positive Pressure venting materials. The vent must be sized in accordance with AERCO’s recommendations.

Water heater plant piping shall be field constructed of materials as specified. Each water heater shall have individually isolating shutoff valves by installing contractor for service and maintenance. Each natural gas water heater shall require a minimum gas pressure of 3” W.C. at gas flow rates indicated in the table below (full load rated capacity). For applications with gas supply pressure greater than 13” W.C., each water heater shall be provided with an individual supply gas regulator by installing contractor for proper gas regulation.

| Model | Gas Flow (scfh) |
| --- | --- |
| AM 199R | 199 |
| AM 250R | 250 |
| AM 399R | 399 |
| AM 500R | 500 |

WARRANTY

The pressure vessel/heat exchanger of the water heater shall carry a prorated 7 year warranty against failure due to condensate corrosion, thermal stress, mechanical defects or workmanship. Years 1-5 shall be non-prorated, year six will be covered at 75% and year seven at 50% of the cost of the pressure vessel/heat exchanger.  The buffer thank shall carry a 5 year warranty against failure.  All other components shall carry an 18-month warranty against failure due to defective materials or workmanship. A Warranty Certificate must be issued to the owner from the manufacturer and a copy of warranty must be submitted for engineer’s approval.

FIELD SERVICES

Contractor shall provide the services of a local factory authorized representative to supervise all phases of equipment startup. A letter of compliance with all factory recommendations and installation instructions shall be submitted to the engineer with operation and maintenance instructions.