BENCHMARK BOILERS SKID PACKAGE SYSTEMS

- PART 1 - GENERAL

## 1.1	RELATED DOCUMENTS

A.	Drawings and general provisions of the Contract apply to this Section, including General and Supplementary Conditions and Division 01 Specification Sections.

## 1.2	SUMMARY

A.	This Section includes factory-fabricated and -assembled Benchmark condensing boilers skid mounted on support structure with associated water, gas and condensate piping, electrical wiring, trim and accessories for generating hot water. Standard package systems include either two or three boilers modules which can be installed either indoors or outdoors with enclosure option.

This specification should be used in conjunction with the specifications for individual boiler models that are required to be skid mounted.

## 1.3	SUBMITTALS

- Product Data: Include scope of supply, installation instructions, description of operation and standard of construction.

- Shop Drawings: Include mechanical layout drawings, flow schematic drawing and symbols.

- Wiring Diagrams: Include electrical power distribution, signal, symbols and control wiring.

- Factory Test report: Include hydrostatic test report included in submittals.

- Warranty: Standard warranty specified in this Section.

- Proof of UL listings.

1.4	QUALITY ASSURANCE

- U.L. Compliance: Electrical panels for package system must be in accordance with U.L. standard 508.

- ASME Compliance:

  - Welds for package system piping must be in accordance with ASME standard 31.1. Welders shall be ASME Section IX certified.

  - Pressure vessels for package systems must be in accordance with ASME standard section 8.

- ANSI Compliance:

  - Package system piping must be in accordance with ANSI Standard 120/53 for steel pipe,

  - Steel flange fittings in accordance with ANSI Standard B16.5 Class 150 and 300,

  - Steel butt-weld fittings in accordance with ANSI Standard B16.9,

  - Cast iron threaded fittings in accordance with ANSI Standard B16.4 Class 125 and 250,

  - Cast iron flange fittings in accordance with ANSI Standard B16.1 Class 125 and 250

  - Valves in accordance with ANSI Standards B16.1, B16.18, B16.24 and B16.34.

- ASTM Compliance: Flange bolts must be in accordance with ASTM Standard 307 Grade B.

- AISC Compliance: Structural Base must be constructed in accordance with American Institute of Steel Construction.

- Uniform Building Code Compliance: Isolation must be constructed in accordance with Uniform Building Code Section 2312; 1 G or less Minimum Restraint Capability.

- Hydraulic Institute Compliance: Pumps must be in accordance with Hydraulic Institute Standard.

- Equipment shall bear the UL factory-listing label for the entire package assembly.

- Structural frame and pipe supports welders shall be AWSD1.1 certified.

1.5	COORDINATION

A.	The contractor shall off-load, store, locate, level, anchor, pipe and wire the system and the remote components in accordance with manufacturer’s instructions.

B. 	Concrete, reinforcement and formwork requirements are specified in Division 03.

1.6	WARRANTY

A.	Standard Warranty for skid package: With respect to items of equipment manufactured, AERCO provides a warranty that such equipment will be free from defect of workmanship and material, for one (1) year after start-up but not exceeding eighteen (18) months after shipment. Should any material prove defective within this time frame, AERCO will repair or replace, at Company’s option, without charge, said defective part or parts F.O.B. AERCO’s shop which is determined to have been defective at the time of shipment. With respect to items of equipment not manufactured by AERCO, AERCO will extend the manufacturer’s warranty in lieu of all other warranties. This paragraph does not cover ordinary wear and tear, corrosion, or improper handling or storage after leaving AERCO’s point of shipment. AERCO shall not be held liable for any contingent damages or delays and will make no allowance for repairs or alterations made by the Buyer, unless made with the prior written consent of an Officer of AERCO.

No express warranties and no implied warranties whether of merchantability or fitness for any particular use, or otherwise (except as to title), other than those expressly set forth above which are made expressly in lieu of all other warranties, shall apply to products sold by AERCO, and no waiver, alteration, or modification of the foregoing conditions shall be valid unless made in writing and signed by an executive officer of AERCO.  In no event shall AERCO have any liability of any kind for indirect, special or consequential damages.

AERCO assumes no responsibility for compliance with any regulations, codes, standards, or ordinances applicable to the installation, location, operation or maintenance.

PART 2 – PRODUCTS

2.1	MANUFACTURERS

A.	Available Manufacturers: Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

B.	Manufacturers: Subject to compliance with requirements, provide products by one of the following:

C.	Basis-of-Design Product: Subject to compliance with requirements, provide AERCO International, Benchmark boilers skid mounted on structural base with single point connection water supply and return piping common headers including fittings, neutralized condensate drain, fuel supply, vents and electrical power. Electrical power panel boxes and controls for package systems shall be factory wired with all wiring requirements.

2.2	CONSTRUCTION

- All components shall be mounted on a structural steel base.  The base shall be large enough to support the packaged system's boilers, piping, and electrical).  Steel supports shall be welded to the base to support the piping and electrical. Both the base and supports shall consist of structural steel components, all welded per the AISC Manual of Steel Construction, Part 4, "Welded Joints".

- The base shall be covered with a ¼” treadplate decking.

- The package piping shall consist of fabricated welded steel headers.  All piping for the system shall be as indicated on the drawings.  Branch piping to the boilers shall be sized for the design capacity of the boiler.  Supports shall be provided for the headers.  Piping supports shall include insulation protection saddles.  The branch suction and discharge piping on each boiler shall be supported independently of boiler connections.  Drain plugs shall be provided at all low points in the system piping where water can be trapped.  Manual air vents shall be provided at all high points in the system piping where air can be trapped.

- Boiler gas connections to be piped to a common point of connection as indicated on the drawings. Piping to be ASTM A53B carbon steel black pipe schedule 40.

- Boiler condensate connections to be piped to a common point of connection as indicated on the drawings. Each boiler includes a condensate trap piped to condensate neutralizer(s) with PVC ASTM D1785 pipe and fittings.

- Butterfly valves shall be furnished on the inlet and outlet of each boiler. Valves 6" and smaller shall be provided with lever operators and valves 8" and larger shall be provided with hand wheel and gear operator.

- Boiler isolation control valves with electric actuator shall be provided as part of the packaged system.

- System shall include Nema 1 single point power circuit breaker panel. All wiring to UL and NEC standards.

2.3	CONTROLS

- Refer to Division 23, Section “Instrumentation and Control of HVAC.”

- Each boiler shall have integrated Boiler Sequencing Technology (BST), capable of multi-unit sequencing with lead-lag functionality and parallel operation.  The system will incorporate the following capabilities:

- Efficiently sequence 2-to-8 units on the same system to meet load requirement.

- Integrated control and wiring for seamless installation of isolation valve. The system shall operate one motorized valve per unit as an element of load sequencing.  Valves shall close with decreased load as units turn off, minimum of one must always stay open for recirculation.

- Automatically rotate lead/lag amongst the units on the chain and monitor run hours per unit and balance load in an effort to equalize unit run hours.

- Designated master control, used to display and adjust key system parameters.

- Automatic bump-less transfer of master function to next unit on the chain in case of designated master unit failure; master/slave status should be shown on the individual unit displays.

- Designated master control, used to display and adjust key system parameters.

- For boiler plants greater than 8 units, the Boiler Manufacturer shall supply as part of the boiler package a completely integrated AERCO Control System (ACS) to control all operation and energy input of the multiple boilers heating plant. The ACS shall be comprised of a microprocessor based control utilizing the MODBUS protocol to communicate with the Boilers via the RS-485 port.  One ACS controller shall have the ability to operate up to 32 AERCO boilers.

The controller shall have the ability to vary the firing rate and energy input of each individual boiler throughout its full modulating range to maximize the condensing capability and thermal efficiency output of the entire heating plant.  The ACS shall control the boiler outlet header temperature within +2ºF.  The controller shall be a PID type controller and uses Ramp Up/Ramp Down control algorithm for accurate temperature control with excellent variable load response.  The ACS controller shall provide contact closure for auxiliary equipment such as system pumps and combustion air inlet dampers based upon outdoor air temperature.

The ACS shall have the following anti-cycling features:

- Manual designation of lead boiler and last boiler.

- Lead boiler rotation at user-specified time interval.

- Delay the firing/shutting down of boilers when header temperature within a predefined deadband.

When set on Internal Setpoint Mode, temperature control setpoint on the ACS shall be fully field adjustable from 50ºF to 190ºF in operation.  When set on Indoor/Outdoor Reset Mode, the ACS will operate on an adjustable inverse ratio in response to outdoor temperature to control the main header temperature.  Reset ratio shall be fully field adjustable from 0.3 to 3.0 in operation.  When set on 4ma to 20ma Temperature Control Mode, the ACS will operate the plant to vary header temperature setpoint linearly as an externally applied 4-20 ma signal is supplied.

When set on MODBUS Temperature Control Mode, the ACS will operate the plant to vary header temperature setpoint as an external communication utilizing the MODBUS protocol is supplied via the RS-232 port. The ACS controller shall have a vacuum fluorescent display for monitoring of all sensors and interlocks.  Non-volatile memory backup of all control parameters shall be internally provided as standard.  The controller will automatically balance the sequence of operating time on each boiler by a first-on first-off mode and provide for setback and remote alarm contacts.  Connection between central ACS system and individual boilers shall be twisted pair low voltage wiring, with the boilers ‘daisy-chained’ for ease of installation.

2.4	ELECTRICAL POWER

- Controllers, Electrical Devices and Wiring: Electrical devices and connections are specified in Division 26 sections.

- Single-Point Field Power Connection: Factory-installed and factory-wired power panel shall have single inlet electrical connection for complete boiler skid package. Power panel shall be factory wired to all boilers and electrical devices on the package.

- Connect wiring according to Division 26 Section "Low-Voltage Electrical Power Conductors and Cables."

- Electrical Characteristics:

| Boiler Model | No. of Units on Package | Voltage | Phase | Frequency | FLA | MCA | MOCP |
| --- | --- | --- | --- | --- | --- | --- | --- |
| BMK750 | 2 | 120 | 1 | 60 | 26 | 30 | 40 |
|  | 3 | 120 | 1 | 60 | 39 | 43 | 50 |
| BMK1000 | 2 | 120 | 1 | 60 | 26 | 30 | 40 |
|  | 3 | 120 | 1 | 60 | 39 | 43 | 50 |
| BMK1500 | 2 | 120 | 1 | 60 | 32 | 36 | 50 |
|  | 3 | 120 | 1 | 60 | 48 | 52 | 70 |
| BMK2000 | 2 | 120 | 1 | 60 | 32 | 36 | 50 |
|  | 3 | 120 | 1 | 60 | 48 | 52 | 70 |
| BMK2500 | 2 | 208 | 3 | 60 | 20 | 23 | 30 |
|  | 3 | 208 | 3 | 60 | 30 | 33 | 40 |
| BMK2500 | 2 | 460 | 3 | 60 | 10 | 12 | 15 |
|  | 3 | 460 | 3 | 60 | 15 | 17 | 20 |
| BMK3000 | 2 | 208 | 3 | 60 | 20 | 23 | 30 |
|  | 3 | 208 | 3 | 60 | 30 | 33 | 40 |
| BMK3000 | 2 | 460 | 3 | 60 | 10 | 12 | 15 |
|  | 3 | 460 | 3 | 60 | 15 | 17 | 20 |
| BMK6000 | 2 | 208 | 3 | 60 | 38 | 43 | 60 |
|  | 3 | 208 | 3 | 60 | 57 | 62 | 80 |
| BMK6000 | 2 | 460 | 3 | 60 | 24 | 27 | 40 |
|  | 3 | 460 | 3 | 60 | 36 | 39 | 50 |
| BMK6000 | 2 | 575 | 3 | 60 | 16 | 18 | 25 |
|  | 3 | 575 | 3 | 60 | 24 | 26 | 35 |

2.5	VENTING

A.	The exhaust vent must be UL Listed for use with Category II, III and IV appliances and compatible with operating temperatures up to 230°F, condensing flue gas service.

- BMK750 and BMK1000 boilers can be used with AL-29-4C, VP1738A, polypropylene, PVC or CPVC vent materials.

- BMK1500, BMK2000, BMK2500, BMK3000 and BMK6000 can be used with Polypropylene and Al 29-4C stainless steel vent materials.

- The minimum exhaust vent duct size for each boiler is:

| Boiler Model | Minimum Exhaust Vent Size |
| --- | --- |
| BMK750 | 6-inch diameter |
| BMK1000 | 6-inch diameter |
| BMK1500 | 6-inch diameter |
| BMK2000 | 8-inch diameter |
| BMK2500 | 8-inch diameter |
| BMK3000 | 8-inch diameter |
| BMK6000 | 12-inch diameter. The minimum exhaust vent duct size when compliance for 9 ppm NOx (corrected to 3% excess oxygen) is required is 14-inch diameter. |

C.	Combustion-Air Intake: Boilers shall be capable of drawing combustion air from the outdoors via a metal or PVC duct connected between the boiler and the outdoors.

D.	The minimum sealed combustion air duct size for each boiler is:

| Boiler Model | Minimum Combustion Air Duct Size |
| --- | --- |
| BMK750 | 6-inch diameter |
| BMK1000 | 6-inch diameter |
| BMK1500 | 6-inch diameter |
| BMK2000 | 8-inch diameter |
| BMK2500 | 8-inch diameter |
| BMK3000 | 8-inch diameter |
| BMK6000 | 14-inch diameter |

E.	Common vent and common combustion air must be an available option for boiler installation. Consult manufacturer for common vent and combustion air sizing.

F.	Follow guidelines specified in manufacturer’s venting guide.

2.6	SOURCE QUALITY CONTROL

- Hydrostatic Test: All piping shall subject to a hydrostatic test. The components shall be tested unpainted. The piping shall be filled with clean water. A hydrostatic pump then pressurizes the system to 150 psig and the pressure shall be maintained for 30 minutes. The gauge on the test pump is checked to make sure the pressure is maintained. The piping is then inspected and checked for leaks or damage. If leaks are detected, the leaks are repaired and the test is redone. The system is drained and the check valves are tested to make sure they are closing. A certified report is filled out and kept in the job file and is available for review.

- Allow Owner access to source quality-control testing of boilers. Notify Architect fourteen days in advance of testing.

- All wiring and electrical to be tested at the factory prior to shipment.

PART 3 - EXECUTION

3.1	EXAMINATION

- Before boiler package(s) installation examine roughing-in for concrete equipment bases, anchor-bolt sizes and locations and piping and electrical connections to verify actual locations, sizes and other conditions affecting boiler performance, maintenance and operations.

  - Final boiler package(s) locations indicated on Drawings are approximate. Determine exact locations before roughing-in for piping and electrical connections.

- Examine mechanical spaces for suitable conditions where boiler package(s) will be installed.

- Proceed with installation only after unsatisfactory conditions have been corrected.

  - BOILER PACKAGE(S) INSTALLATION

- Install boiler package(s) level on concrete bases. Concrete base is specified in Division 23 Section "Common Work Results for HVAC," and concrete materials and installation requirements are specified in Division 03.

- Package systems shall be installed in accordance with AERCO’s installation recommendations and instructions.

  - CONNECTIONS

- Piping installation requirements are specified in other Division 23 sections. Drawings indicate general arrangement of piping, fittings and specialties.

- Class 150 flanged HWS & HWR connections

- Condensate drain PVC connection

- Gas Pipe Connection NPT or Class 150 flanged

- Install piping from safety relief valves to nearest floor drain.

- Boiler Venting

  - Install flue venting kit and combustion-air intake.

  - Connect venting full size to boiler connections. [Comply with requirements in Division 23 Section "Breechings, Chimneys and Stacks."]

- Electrical wiring connection main power distribution panel. See plans for voltage and size.

- Control wiring connection as required to each boiler

- Ground equipment according to Division 26 Section "Grounding and Bonding for Electrical Systems."

  - FIELD QUALITY CONTROL

A.	Perform tests and inspections and prepare test reports.

1.	Manufacturer's Field Service: Engage a factory-authorized service representative to inspect components, assemblies and equipment installations, including connections, to assist in testing and training the operator.

B.	Tests and Inspections

1.	Perform installation and startup checks according to manufacturer's written instructions.

2.	Perform hydrostatic test. Repair leaks and retest until no leaks exist.

3.	Start units to confirm proper motor rotation and unit operation. Adjust air-fuel ratio and combustion.

4.	Test and adjust controls and safeties. Replace damaged and malfunctioning controls and equipment.

- a.	Check and adjust initial operating set points and high- and low-limit safety set points of fuel supply, water level and water temperature.

- b.	Set field-adjustable switches and circuit-breaker trip ranges as indicated.

C.	Remove and replace malfunctioning units and retest as specified above.

D.	Occupancy Adjustments: When requested within 2 months of date of Substantial Completion, provide on-site assistance adjusting system to suit actual occupied conditions. Provide up to two visits to Project during other than normal occupancy hours for this purpose.

E.	Performance Tests:

The boiler manufacturer is expected to provide partial load thermal efficiency curves. These thermal efficiency curves must include at least three separate curves at various BTU input levels. If these curves are not available, it is the responsibility of the boiler manufacturer to complete the following performance tests:

- Engage a factory-authorized service representative to inspect component assemblies and equipment installations, including connections, and to conduct performance testing.

- Boilers shall comply with performance requirements indicated, as determined by field performance tests. Adjust, modify, or replace equipment to comply.

- Perform field performance tests to determine capacity and efficiency of boilers.

- a.	Test for full capacity.

- b.	Test for boiler efficiency at [low fire 20, 40, 60, 80, 100, 80, 60, 40 and 20] percent of full capacity. Determine efficiency at each test point.

- Repeat tests until results comply with requirements indicated.

- Provide analysis equipment required to determine performance.

- Provide temporary equipment and system modifications necessary to dissipate the heat produced during tests if building systems are not adequate.

- Notify Architect in advance of test dates.

- Document test results in a report and submit to Architect.

  - ENCLOSURE (Optional for outdoor installation)

- General: The system shall be enclosed in an assembled pre-fabricated metal building with mounted and wired accessories as specified. The building shall include State certification. Each building shall be supplied complete with all necessary component parts, including drill in foundation anchors, to form a complete building system and all parts shall be new and free from all defects or imperfections. The building width and length shall be measured from the outside of the building wall panels and the height of the building shall be the distance measured from the bottom surface of the base channel to the exterior juncture of the roof and sidewall panels. The building shall be supplied in three pieces to accommodate shipping limitations

- Construction:

  - Roof panels shall be supplied in a single continuous length from eave line to ridge line and shall be designed to tightly interlock so that no fasteners are required at intermediate points along the panel side laps.Roof panels shall be 16" or 12" wide with a smooth surface between the interlocking side ribs.  The interlocking ribs shall be a minimum 3" high, and shall be turned upward.  All roof panels shall be factory punched for connection at the eave line of the building.There shall be no fastener penetrations through the roof covering except at eave lines, ridgelines and roof accessory openings such as skylights and ventilators.Roof panels shall be a nominal 24 gauge steel coated on both sides with a coating of corrosion resistant aluminum-zinc alloy conforming to ASTM A-792 specification with the coating conforming to AZ55 (55%) standard by a continuous hot dipping process.  Coating weight shall be a minimum of 0.32 oz. of aluminum-zinc alloy per square foot of coated sheet equivalent to about 0.75-mil thickness on each side.  Minimum yield strength of panel material shall be 50,000 PSI.

  - Exterior wall panels of the building shall be a single continuous length from the base channel to the roofline of the building at the sidewalls and endwalls of the building, except where interrupted by wall openings.Wall panels shall be 16" wide with a 3" deep inward turned interlocking side rib.  Wall panels shall contain two 3/4" deep by 3-1/8" wide fluted recesses, each starting 2-7/16" from the panel edge.

Wall panels shall be fastened internally to the base channel and eave cap of the building with 3/8" diameter electro-galvanized machine bolts placed within the panel interlock.  The fastening system shall be designed so that no wall fasteners are exposed on the exterior surface of the walls. Wall panels shall be nominal 24 gauge galvanized steel conforming to ASTM A-653 specifications with the galvanized coating conforming to G90 (1.25 oz. Commercial) standards.  Minimum yield strength of panel material shall be 40,000 PSI.  Panel material shall be embossed with a random pattern pebble embossure of approximately .007 - .008 depth.

All exterior surfaces of the galvanized steel wall covering and exterior trim shall receive a factory, roller applied, paint coating having an exterior coating thickness of 0.8 to 1.2 mils of dry film thickness.  The finish coat for wall panels shall be a siliconized polyester formulation in a standard Parkline color.

The wall panel color coating shall carry a low fire hazard rating equal to a Class 1 material as defined by Factory Mutual.  The panel coating shall have achieved a Flame Spread Index of 0 and a Fuel Contributed Index of 5 or less when tested in accordance with ASTM E-84 test procedures.

Exterior color coatings shall meet the following performance standards after 10 years continuous exposure in normal atmospheric conditions not containing corrosive fumes such as chemical fumes or salt spray. Panels shall show no evidence of blistering, peeling, or chipping. Panels shall not show surface chalking in excess of the No. 8 rating D659 as established by the American Society of Testing Materials (ASTM).

Panels, after cleaning, shall not show color change in excess of five (5) NBS units when measured in accordance with the ASTM-D-2244 standard.

  - All doors shall be 1-3/4" thick flush-type.  Door panels shall be nominal 20 gauge galvanized steel reinforced by lamination to a honeycomb core enclosed with 16 gauge end channel.  The hinge reinforcements shall be nominal 7 gauge and the lock reinforcements shall be nominal 16 gauge. Door frames shall be 4-3/4" deep double rabbeted type of nominal 16 gauge galvanized steel. Doors and frames shall be factory painted with one coat of baked on primer.  All doors shall be pre-assembled in their frames and hardware installed and tested prior to shipment.  Field installation of single leaf door units shall not require any frame assembly or door hanging.

Door hardware shall consist of:

3 - 4-1/2" x 4-1/2" standard weight plain bearing hinges per ANSI #A5133, 630 satin stainless finish with non-rising pins.

3-11/16" wide x 5/8" high extruded-aluminum threshold.  (Out Swing)

1/4" x 1/2" silicone rubber weather-stripping.

Mortise lockset per ANSI A156.13, Series 1000, Grade 1, Function F13, 626 satin chrome finish (levers both sides).

  - The building manufacturer shall supply all necessary framing and connectors to structurally replace the panels removed by any wall opening.  All trim and flashings required to make weather-tight the unit placed in any opening shall be provided by the supplier of the unit being installed.

  - The interior of the metal walls shall be lined with 32" wide, nominal 26 gauge galvanized steel panels, prepainted Arctic White with 1/4" high by 1" wide flutes on 8" centers. The exterior panel void shall have 3-1/2" thick R11 unfaced fiberglass insulation.  The liner system shall be furnished complete with White base molding and White trim.

The "U" value of the finished wall system shall be 0.16 BTU's per square foot when calculated in accordance with the "Zone Method" contained in ASHRAE "Handbook of Fundamentals", 1981 edition.

FWL-PER
The liner shall have 1/8" diameter perforations spaced on 3/8" staggered centers. The complete wall system shall have been certified by an independent testing laboratory to have a minimum NRC rating of 0.90 when tested in accordance with ASTM C423 standards.

  - Roof insulation shall consist of 48" wide, 3" thick, 6# density fiberglass faced on its exposed side with a white metalized polypropylene scrimkraft facing.  The faced insulation material shall have a UL Flame Spread Rating of 25 when tested in accordance with UL 723 or ASTM E-84 procedures. Insulation shall be supported at the roof line by means of mechanical clips spaced on maximum 4' centers and shall be sealed by means of a 2" side tabs on the facing. The "U" value through the insulated roof shall be a maximum of 0.10 BTU's per square foot when calculated in accordance with the "Zone Method" contained in ASHRAE "Handbook of Fundamentals", 1981 edition.

- ENCLOSURE ACCESSORIES:

  - Access Doors

  - Building heater

  - Exhaust fans and louvers

  - Interior, exterior and emergency lights

  - Convenience receptacles