Furnish and install as shown on plans in accordance with all codes and authorities having jurisdiction ___water heater(s), Model____________, as manufactured by AERCO INTERNATIONAL INC.

Each heater shall be rated to heat: _____ GPM of water from _____°F to _____°F when supplied with _____ GPM of boiler water _____°F to the control valve.

Design & Construction:

Each heater shall be of the counter-current flow stainless steel brazed plate heat exchanger designed and manufactured in accordance with ASME Code Section VIII, Div. 1 for 435 psig @ 300ºF.  The packaged heater shall be rated for not less than (select one)

□ 150 psig

□ 200 psig

on the service water side and not less than 150 PSIG, 250°F on the boiler water side.  The plates shall be 316L stainless steel, brazed together using copper.

Electronic Control System:

The heater shall maintain +/- 2°F Max temperature fluctuation from temperature setpoint at 0% to 100 % load at a constant load and +/- 4°F under normal diversified domestic load conditions.  The system shall consist of a 3-way electronic control valve, constant speed domestic water circulator pump, control panel enclosure housing a PID temperature controller with digital indication of shell outlet water temperature, boiler water inlet and boiler water outlet temperatures, digital over-temperature limit switch, and feed-forward and feedback temperature sensors. The controller shall close the control valve in an over-temperature condition.  The system shall have the following additional characteristics:

- Controller temperature setpoint range between 50°F to 180°F maximum

- Configured for 120V/1Phase/60 Hz, 220V/1Phase/60 Hz and 220V/1Phase/50 Hz

- Easy start-up. Dial in setpoint & walk away.

The electronic control valve shall be of equal percentage flow characteristics, and has a tight shut-off with low leakage rate of .02% of its Cv value.  The valve shall have the following performance characteristics:

- 1000 to 1 Turndown.

- Magnetic Actuator with Fail Closed Design-particularly on loss of power

- Time to Full Open Position: 2 seconds

- Time to Full Closed Position: 2 seconds

- The PID temperature controller shall incorporate a feed-forward function and be password protected.   The controller either ___shall or ___shall not be capable of remote communications via an optional add-in board that incorporates either: ___ RS-232 port or ___RS-485 port & utilizes the MODBUS protocol for interoperability with Building Automation Systems (BAS).

- Controls interface with BACnet, Lonworks, and N2 shall utilize an  ___ optional AERCO Communications Gateway to act as a MODBUS interface/translator between the BAS and the MODBUS port of the temperature controller.  The AERCO Communications Gateway shall be comprised of a microprocessor based control utilizing the MODBUS protocol to communicate with the temperature controller.  Non-volatile backup of all point mappings and programs shall be internally provided as standard.  Connection between Gateway and individual water heaters shall be “daisy chain” with shielded, twisted pair, low voltage wiring for ease of installation.

The following information shall be accessible locally at the controller or remotely via the communications port:

- Setpoint – can be changed remotely

- Outlet Temperature

- Over Temperature Alarm

- Control Output Signal to valve

Each heater shall be supplied by the manufacturer ready to accept existing boiler water and domestic water lines, and furnished with the following accessories:

- Y-strainers with blowdown valve for boiler water and domestic water.

- Boiler water strainer differential pressure gauge.

- Bronze T & P relief valve, conforming to ANZI Z21.22, set at 150 PSIG/210°F or Pressure Relief Valve set at 200 PSIG

- Bronze ball type isolation valves.

- 3/4" Bronze domestic water drain valve.

- Domestic water Air Vent rated for either 150 PSIG operation or 200 PSIG operation accordingly.

- In-place connections for easy and simple cleaning of the brazed plate heat exchanger.

Warranty:

The heater shall carry the following manufacturer's warranty from date of shipment:

The Heat Exchanger shall carry a 5-year warranty and all other parts/components shall carry an 18-month warranty against mechanical failure or workmanship from the date of shipment.